## Tunnel heat gain analysis
2018 UGA Tunnel-Ventilated Poultry House Heat Gain Analysis (v1.2) | [6 empty] | Ceiling | 30149.6269 | ft2
The University of Georgia Department of Poultry Science - Michael Czarick (mczarick@uga.edu) | [6 empty] | End walls | 1140 | ft3
This spreadsheet calculates the minimum tunnel fan capacity required to insure the air exchange rate is high enough that | [6 empty] | Upper side walls | 2000 | ft4
under the conditions inputted that there will be no more than a 5 F temperature difference between the tunnel inlet and | [6 empty] | Lower side walls | 2000 | ft5
exhaust fan end of the house. Additional tunnel fan capacity may be required to obtain adequate bird cooling/wind chill effect | [6 empty] | Curtains | 3000 | ft6
Only green values can be modified | [6 empty] | Foundation | 0 | ft7
[7 empty] | Wall Delta T | 10 | F
| Do you want to display equivalent metric values (yes = 1, no = 0)? | 1 |  |  |  |  | Ceiling Delta t | 50 | F
[7 empty] | Ceiling | 125623.4453 | btu/s/hr
| Design conditions: |  | Metric |  |  |  | End walls | 950 | btu/s/hr
| Inside temperature (F) | 85 | 29.4444 |  |  |  | Upper side walls | 1666.6667 | btu/s/hr
| Outside temperature (F) | 95 | 35 |  |  |  | Lower side walls | 1666.6667 | btu/s/hr
| "Attic" temperature (F) (Open ceiling = 150, Dropped ceiling = 135) | 135 | 57.2222 |  |  |  | Curtains | 20000 | btu/s/hr
[7 empty] | Foundation | 0 | btu/s/hr
| Basic house information: | [5 empty] | Lights | 4335 | btu/s/hr
| House length | 500 | 152.5 |  |  |  | Birds | 1333000 | btu/s/hr
| House width | 60 | 18.3 |  |  |  | Total | 1487241.7786 | btu/s/hr
| Total side wall height | 8 | 2.44 |  |  |  | Total side wall | 23333.3333 | btu/s/hr
| Peak ceiling height | 11 | 3.355
| Open or Dropped ceiling (o/d) | d | d
| Bird information: |  | Metric
| Number of birds | 43000 | 43000
| Bird weight (lbs) | 5 | 2.2727
| Heat production per pound | 6.2 | 3.9965
| Pounds per square foot | 7.1667 | 35.0164
Side wall construction (For houses without curtains and/or foundations, lower sidewalls, etc enter "0" for height)
| Curtain height | 3 | 0.915
| Upper side wall height | 2 | 0.61
| Lower side wall height | 2 | 0.61
| Stem/foundation wall height | 0 | 0
Lighting:
| Number of light bulbs | 150 | 150
| Light bulb wattage | 10 | 10
| House surface insulation values (hr/btu*ft2*F) | (enter "0" for blank values) | Metric
| Ceiling R-value | 12 | 2.112
| End wall R-value | 12 | 2.112
| Upper side wall R-value | 12 | 2.112
| Lower side wall R-value | 12 | 2.112
|  | 0 | 0
| Curtain R-value | 1.5 | 0.264
Tunnel fan information:
| Approximate air moving capacity of tunnel fans (cfm) | 25000 | 42500 | Ceiling | 125623.4453 | 8.447%
|  |  |  | Lights | 4335 | 0.2915%
Results: |  |  | Metric
Total poultry house heat load = |  | 1487241.7786 | 432787.3576 | End walls | 950 | 0.06388%
Minimum tunnel fan capacity = |  | 277989.1175 | 472581.4997
Approximate number of tunnel fans = |  | 11.1196 | 11.1196
Average air speed = |  | 487.7002 | 2.4385 | Upper side walls | 1666.6667 | 0.1121%
Temperature difference from tunnel inlet end to fan end = |  | 5 | 2.7778 | Curtains | 20000 | 1.345%
Cfm per square foot of floor space = |  | 9.2663 | 169.3385 | Lower side walls | 1666.6667 | 0.1121%
Cfm per bird = |  | 6.4649 | 10.9903
Btu's/hr per square foot |  | 49.5747 | 155.0792 | Birds | 1333000 | 89.63%
|  |  |  | Total | 1487241.7786
Change tunnel fan capacity from minimum?
Tunnel fan capacity (cfm) = |  | 360000 | 612000
Approximate number of tunnel fans required = |  | 14.4 | 14.4
Temperature difference from tunnel inlet end to fan end = |  | 3.861 | 2.145
Average air speed = |  | 631.5789 | 3.1579
Cfm per square foot of floor space = |  | 12 | 219.2959
Cfm per bird = |  | 8.3721 | 14.2326
Estimated pad area (1 ft2 per 350 cfm of modified tunnel fan capacity) |  |  | Metric
Required evaporative cooling pad area |  | 1028.5714 | 95.6829
Total pad length (5' tall pad) |  | 205.7143 | 62.7429
Total pad length (6' tall pad) |  | 171.4286 | 52.2857
Side wall inlet system design (1 ft2 per 750 cfm of min. tunnel fan capacity) |  |  | Metric
Desired side wall inlet capacity (40 to 60 % of minimum tunnel fan capacity) |  | 50 | 50
Side wall opening height (inches) |  | 10 | 25.4
Side wall opening length (inches) |  | 42 | 106.68
Total side wall inlet area |  | 185.3261 | 17.24
Number of side inlets required |  | 63.5404 | 63.5404
Stem wall/foundation
Side wall
Upper side wall
Lower side wall
Curtain opening
Dropped ceiling
Open ceiling
Curtain side wall
Broiler heat production (Btu's/hr per lb.):
4 lb. = 6.6
5 lb. = 6.2
6 lb. = 5.9
8 lb.+ = 5.4
Other types of poultry (Btu's/hr per lb.):
Broiler pullets = 3.5
Broiler breeders = 4
Turkeys (heavy toms) = 4
Turkey poults (brooder barn) = 7
Commerical layers = 3.5
Totally enclosed side wall
Stem wall/foundation
Lower side wall
Upper side wall
Curtain opening
Curtain side wall

## Tunnel fan comparison
Tunnel-Ventilated Broiler House Fan Comparison 2018 | [9 empty] | 190000
The University of Georgia Department of Poultry Science - Michael Czarick (mczarick@uga.edu)
Enter green values in all sections (don't enter "$" or "," )
Do you want to display equivalent metric input values (yes = 1, no = 0)? |  |  | 0
[9 empty] | Energy Eff. | Pressure
Input poultry house information | [8 empty] | Rating | Rating
House length= |  | 500 | 152.5 | Electricty rate ($ per kw*hr) = |  | 0.13 | 0.1 |  | 2 | 4 | 1
House width= |  | 40 | 12.2 | Estimated yearly operating hours = |  | 3000 | 3000 |  | 2 | 4 | 1
Side wall height= |  | 8 | 2.44 | Minimum design air velocity = |  | 700 | 3.5
Ceiling peak height= |  | 11 | 3.355 | Minimum tunnel fan capacity (cfm/ft2) = |  | 9.5 | 173.6092 |  | 2 | 4 | 1
|  |  |  | Total minimum tunnel fan capacity (cfm) = |  | 190000 | 323000
[9 empty] | cfm for velocity | velocity check
Tunnel fan information | [8 empty] | 266000 | 266000
Tunnel Fan Model | Air Flow (0.05") | Air Flow (0.10") | Air Flow (0.15") | Air Flow(0.20") | Energy Efficiency | Air Flow Ratio | Price of Fan | 266000 | 266000
[5 empty] | cfm/watt @ 0.10" | (calculated) | ($) | 266000 | 266000
name | 20000 | 20000 | 20000 | 20000 | 20 | 1 | 1000 | 266000 | 266000
name | 20000 | 20000 | 20000 | 20000 | 20 | 1 | 1000
name | 20000 | 20000 | 20000 | 20000 | 20 | 1 | 1000
name | 20000 | 20000 | 20000 | 20000 | 20 | 1 | 1000
Tunnel fans required
Tunnel Fan Model | Design static | Tunnel Fan | Number of fans | Total air moving capacity | Total fan operating | Average air speed
| pressure | capacity | required * | at design static pressure | cost (yearly) * | (all fans operating)
name | 0.15 | 20000 | 13 | 260000 | 5070 | 680 | 3.4
name | 0.15 | 20000 | 13 | 260000 | 5070 | 680 | 3.4
name | 0.15 | 20000 | 13 | 260000 | 5070 | 680 | 3.4
name | 0.15 | 20000 | 13 | 260000 | 5070 | 680 | 3.4
Total fan cost
Tunnel Fan Model |  | Five Year |  | Ten Year
| Total fan cost | Electricity cost | Total cost | Electricity cost | Total cost
name | 13000 | 25350 | 38350 | 50700 | 63700
name | 13000 | 25350 | 38350 | 50700 | 63700
name | 13000 | 25350 | 38350 | 50700 | 63700
name | 13000 | 25350 | 38350 | 50700 | 63700
Minimum ventilation tunnel fan capacity to insure more than a 5 temperature rise typically requires between 9 and 11 cfm/ft2 of floor area. A more precise minimum tunnel fan capacity can be determined by using the UGA Poultry House Heat Gain Spreadsheet.
Estimated yearly operating hours can be very difficult to estimate. On average for a producer
growing a large broiler the average number of operating hours per fan is between 1,750 and 2,500
hours. For producers growing smaller birds the average tunnel fan operating hours is often 30%
or lower.
More details on Tunnel performance fan ratings can be found at
www.poultryventilation.com (https://www.poultryventilation.com/tips/vol24/n12)

## Evap cooling system design (hidden)
Evaportive Cooling Pad System Design 2018
The University of Georgia Department of Poultry Science - Michael Czarick (mczarick@uga.edu)
Enter green values in all sections
Do you want to display equivalent metric values (yes = 1, no = 0)? | 0
Design Conditions:
Tunnel fan capacity (cfm) | 180000 | 306000
Outside temperature (F) | 90 | 32.2222
Outside relative humidity (%) | 50 | 50
Pad height (ft) | 5 | 1.525
System Performance:
| 4" Pad (45 X 45) | 6" Pad (45 X 15) | 10 cm | 15 cm
Design pad velocity (ft/min) | 225 | 350 | 1.125 | 1.75
Minimimum recommended pad area | 800 | 514.2857 | 74.42 | 47.8414
Total pad length | 160 | 102.8571 | 48.8 | 31.3714
Pad static pressure | 0.046687 | 0.05245 | 11.8586 | 13.3223
Evaporative cooling efficiency | 72.9% | 74.45% | 72.9% | 74.45%
Wet bulb / pad temperature | 74.8547 | 74.8547 | 23.8082 | 23.8082
Incoming air temperature | 78.9588 | 78.7236 | 26.0882 | 25.9576
Incoming Rh | 84.2367 | 85.0658 | 84.2367 | 85.0658
Pad water usage | 4.3839 | 4.4482 | 16.6587 | 16.903
Modify Pad Area?
| 4" Pad (45 X 45) | 6" Pad (45 X 15) | 10 cm | 15 cm
Desired total pad length (ft) | 6 | 6 | 1.83 | 1.83
Desired pad height (ft) | 160 | 103 | 48.8 | 31.415
Total pad area | 960 | 618 | 89.304 | 57.4895
Pad velocity | 187.5 | 291.2621 | 0.9375 | 1.4563
Pad static pressure | 0.033984 | 0.037626 | 8.632 | 9.557
Evaporative cooling efficiency | 75.34% | 76.1% | 75.34% | 76.1%
Wet bulb / pad temperature | 74.8547 | 74.8547 | 23.8082 | 23.8082
Incoming air temperature | 78.5894 | 78.474 | 25.883 | 25.8189
Incoming Rh | 85.5428 | 85.9552 | 85.5428 | 85.9552
Pad water usage | 4.4849 | 4.5165 | 17.0426 | 17.1628
Cooling efficiency |  |  | 75.34% | 76.1%
Pad velocity | 225 | 350 | 187.5 | 291.2621
Inside temp | 78.9588 | 78.7236 | 78.5894 | 78.474
inside temp c | 26.0882 | 25.9576 | 25.883 | 25.8189
Outside temperature | 90 | 90 | 90 | 90
Outside relative humidity | 50 | 50 | 50 | 50
Outside C | 32.2222 | 32.2222 | 32.2222 | 32.2222
Outside Rh | 50 | 50 | 50 | 50
Wet bulb (F) | 74.8547 | 74.8547 | 74.8547 | 74.8547
wet bulb C | 23.8082 | 23.8082 | 23.8082 | 23.8082
ESWB | 29.4344 | 29.4344 | 29.4344 | 29.4344
ES (inside) | 33.7116 | 33.4526 | 33.3056 | 33.1796
W | 0.028033 | 0.028092 | 0.028125 | 0.028154
Ws | 0.033279 | 0.033023 | 0.032878 | 0.032754
RH (inside) | 84.2367 | 85.0658 | 85.5428 | 85.9552
pws outside | 48.1593 | 48.1593 | 48.1593 | 48.1593
pws inside | 33.7877 | 33.5276 | 33.38 | 33.2535
pw outside | 24.0796 | 24.0796 | 24.0796 | 24.0796
pw inside | 28.4617 | 28.5206 | 28.5542 | 28.5831
A outside | 0.17094 | 0.17094 | 0.17094 | 0.17094
A inside | 0.20619 | 0.20671 | 0.20701 | 0.20726
A outside english | 0.013297 | 0.013297 | 0.013297 | 0.013297
A inside english | 0.016039 | 0.016079 | 0.016102 | 0.016122
Difference | 0.0027421 | 0.0027823 | 0.0028053 | 0.0028251
gallons per minute | 4.3839 | 4.4482 | 4.4849 | 4.5165

## Pad set temp simulator 2014 (hidden)
Six Inch Evaporative Cooling Pad Set Temperature Simulator | [8 empty] | Day | Hour |  | TIME | Outside T | outside C | Outside Rh | wet bulb | wetbulb c | incoming pads on | inside t | air temp with thermostat | check | Incoming air temp | incoming air temp c | pad on temp | House Rh if pad is on | Rh if pad is off | house rh | w inside | ESWB | wsinside | ES Inside
The University of Georgia Department of Poultry Science - Michael Czarick (mczarick@uga.edu)
Enter pad set temperature | [12 empty] | 76 |  | 90
| Pad set temperature |  | 100 | Avg. house temp | 84.8213 | Avg. House Rh | 71.8707 | 7 | 21 | 1 | 35 | 1997-07-21 01:00 | 95 | 35 | 60 | 83.2789 | 28.4883 | 86.2092 | 30.1162 | 95 | FALSE | 95 | 35 | 100 | 67.8279 | 60 | 60 | 0.037535 | 38.7895 | 0.055339 | 56.058
|  | . | [5 empty] | 7 | 21 | 2 | 25 | 1997-07-21 02:00 | 77 | 25 | 85 | 73.4262 | 23.0145 | 74.3196 | 23.5109 | 77 | FALSE | 77 | 25 | 100 | 88.0682 | 85 | 85 | 0.027478 | 28.061 | 0.031201 | 31.607
|  | . | [5 empty] | 7 | 21 | 3 | 23.8889 | 1997-07-21 03:00 | 75 | 23.8889 | 90 | 72.6805 | 22.6003 | 73.2604 | 22.9224 | 75 | FALSE | 75 | 23.8889 | 100 | 92.0323 | 90 | 90 | 0.026871 | 27.3665 | 0.029198 | 29.5773
|  | . | [5 empty] | 7 | 21 | 4 | 24.4444 | 1997-07-21 04:00 | 76 | 24.4444 | 87 | 72.939 | 22.7439 | 73.7042 | 23.169 | 76 | FALSE | 76 | 24.4444 | 100 | 89.6507 | 87 | 87 | 0.027061 | 27.6055 | 0.030185 | 30.5774
|  | . | [5 empty] | 7 | 21 | 5 | 24.4444 | 1997-07-21 05:00 | 76 | 24.4444 | 87 | 72.939 | 22.7439 | 73.7042 | 23.169 | 76 | FALSE | 76 | 24.4444 | 100 | 89.6507 | 87 | 87 | 0.027061 | 27.6055 | 0.030185 | 30.5774
|  | . | [5 empty] | 7 | 21 | 6 | 24.4444 | 1997-07-21 06:00 | 76 | 24.4444 | 90 | 73.6655 | 23.1475 | 74.2491 | 23.4717 | 76 | FALSE | 76 | 24.4444 | 100 | 92.0277 | 90 | 90 | 0.027779 | 28.287 | 0.030185 | 30.5774
|  | . | [5 empty] | 7 | 21 | 7 | 26.1111 | 1997-07-21 07:00 | 79 | 26.1111 | 85 | 75.372 | 24.0956 | 76.279 | 24.5994 | 79 | FALSE | 79 | 26.1111 | 100 | 88.0279 | 85 | 85 | 0.029334 | 29.946 | 0.033324 | 33.7571
|  | . | [5 empty] | 7 | 21 | 8 | 27.7778 | 1997-07-21 08:00 | 82 | 27.7778 | 77 | 76.2073 | 24.5596 | 77.6555 | 25.3642 | 82 | FALSE | 82 | 27.7778 | 100 | 81.7274 | 77 | 77 | 0.030029 | 30.7885 | 0.036743 | 37.2212
|  | . | [5 empty] | 7 | 21 | 9 | 30 | 1997-07-21 09:00 | 86 | 30 | 68 | 77.5072 | 25.2818 | 79.6304 | 26.4613 | 86 | FALSE | 86 | 30 | 100 | 74.6661 | 68 | 68 | 0.031192 | 32.1406 | 0.041776 | 42.3189
|  | . | [5 empty] | 7 | 21 | 10 | 31.1111 | 1997-07-21 10:00 | 88 | 31.1111 | 65 | 78.4814 | 25.823 | 80.8611 | 27.145 | 88 | FALSE | 88 | 31.1111 | 100 | 72.2525 | 65 | 65 | 0.032159 | 33.1877 | 0.044509 | 45.088
|  | . | [5 empty] | 7 | 21 | 11 | 32.7778 | 1997-07-21 11:00 | 91 | 32.7778 | 62 | 80.3078 | 26.8377 | 82.9809 | 28.3227 | 91 | FALSE | 91 | 32.7778 | 100 | 69.727 | 62 | 62 | 0.034097 | 35.231 | 0.048901 | 49.5367
|  | . | [5 empty] | 7 | 21 | 12 | 33.3333 | 1997-07-21 12:00 | 92 | 33.3333 | 60 | 80.5833 | 26.9907 | 83.4375 | 28.5764 | 92 | FALSE | 92 | 33.3333 | 100 | 68.1196 | 60 | 60 | 0.034364 | 35.5485 | 0.050446 | 51.1019
|  | . | [5 empty] | 7 | 21 | 13 | 33.8889 | 1997-07-21 13:00 | 93 | 33.8889 | 54 | 79.516 | 26.3978 | 82.887 | 28.2705 | 93 | FALSE | 93 | 33.8889 | 100 | 63.4881 | 54 | 54 | 0.033035 | 34.3321 | 0.052033 | 52.7099
|  | . | [5 empty] | 7 | 21 | 14 | 34.4444 | 1997-07-21 14:00 | 94 | 34.4444 | 52 | 79.7081 | 26.5045 | 83.281 | 28.4895 | 94 | FALSE | 94 | 34.4444 | 100 | 61.8602 | 52 | 52 | 0.033197 | 34.5483 | 0.053664 | 54.3616
|  | . | [5 empty] | 7 | 21 | 15 | 34.4444 | 1997-07-21 15:00 | 94 | 34.4444 | 52 | 79.7081 | 26.5045 | 83.281 | 28.4895 | 94 | FALSE | 94 | 34.4444 | 100 | 61.8602 | 52 | 52 | 0.033197 | 34.5483 | 0.053664 | 54.3616
|  | . | [5 empty] | 7 | 21 | 16 | 35 | 1997-07-21 16:00 | 95 | 35 | 49 | 79.5147 | 26.397 | 83.386 | 28.5478 | 95 | FALSE | 95 | 35 | 100 | 59.4647 | 49 | 49 | 0.032907 | 34.3306 | 0.055339 | 56.058
|  | . | [5 empty] | 7 | 21 | 17 | 33.8889 | 1997-07-21 17:00 | 93 | 33.8889 | 52 | 78.84 | 26.0222 | 82.38 | 27.9889 | 93 | FALSE | 93 | 33.8889 | 100 | 61.9848 | 52 | 52 | 0.032253 | 33.5806 | 0.052033 | 52.7099
|  | . | [5 empty] | 7 | 21 | 18 | 33.8889 | 1997-07-21 18:00 | 93 | 33.8889 | 52 | 78.84 | 26.0222 | 82.38 | 27.9889 | 93 | FALSE | 93 | 33.8889 | 100 | 61.9848 | 52 | 52 | 0.032253 | 33.5806 | 0.052033 | 52.7099
|  | . | [5 empty] | 7 | 21 | 19 | 32.7778 | 1997-07-21 19:00 | 91 | 32.7778 | 60 | 79.6847 | 26.4915 | 82.5135 | 28.0631 | 91 | FALSE | 91 | 32.7778 | 100 | 68.2183 | 60 | 60 | 0.033359 | 34.522 | 0.048901 | 49.5367
|  | . | [5 empty] | 7 | 21 | 20 | 29.4444 | 1997-07-21 20:00 | 85 | 29.4444 | 75 | 78.5186 | 25.8437 | 80.1389 | 26.7439 | 85 | FALSE | 85 | 29.4444 | 100 | 80.048 | 75 | 75 | 0.032391 | 33.2283 | 0.040465 | 40.9907
|  | . | [5 empty] | 7 | 21 | 21 | 30 | 1997-07-21 21:00 | 86 | 30 | 72 | 78.6325 | 25.9069 | 80.4744 | 26.9302 | 86 | FALSE | 86 | 30 | 100 | 77.695 | 72 | 72 | 0.032458 | 33.3527 | 0.041776 | 42.3189
|  | . | [5 empty] | 7 | 21 | 22 | 28.8889 | 1997-07-21 22:00 | 84 | 28.8889 | 74 | 77.3016 | 25.1676 | 78.9762 | 26.0979 | 84 | FALSE | 84 | 28.8889 | 100 | 79.3359 | 74 | 74 | 0.031091 | 31.9234 | 0.039189 | 39.6989
|  | . | [5 empty] | 7 | 21 | 23 | 27.7778 | 1997-07-21 23:00 | 82 | 27.7778 | 79 | 76.732 | 24.8511 | 78.049 | 25.5828 | 82 | FALSE | 82 | 27.7778 | 100 | 83.2651 | 79 | 79 | 0.030594 | 31.3281 | 0.036743 | 37.2212
|  | . | [5 empty] | 7 | 21 | 24 | 26.6667 | 1997-07-22 | 80 | 26.6667 | 85 | 76.3449 | 24.6361 | 77.2587 | 25.1437 | 80 | FALSE | 80 | 26.6667 | 100 | 88.0077 | 85 | 85 | 0.030302 | 30.9292 | 0.034432 | 34.8792
|  | . | [5 empty] | 7 | 22 | 1 | 27.2222 | 1997-07-22 01:00 | 81 | 27.2222 | 82 | 76.5487 | 24.7493 | 77.6615 | 25.3675 | 81 | FALSE | 81 | 27.2222 | 100 | 85.6284 | 82 | 82 | 0.030459 | 31.1387 | 0.035571 | 36.0336
|  | . | [5 empty] | 7 | 22 | 2 | 25.5556 | 1997-07-22 02:00 | 78 | 25.5556 | 91 | 75.8818 | 24.3788 | 76.4113 | 24.673 | 78 | FALSE | 78 | 25.5556 | 100 | 92.8254 | 91 | 91 | 0.029934 | 30.4577 | 0.032247 | 32.6666
|  | . | [5 empty] | 7 | 22 | 3 | 26.1111 | 1997-07-22 03:00 | 79 | 26.1111 | 85 | 75.372 | 24.0956 | 76.279 | 24.5994 | 79 | FALSE | 79 | 26.1111 | 100 | 88.0279 | 85 | 85 | 0.029334 | 29.946 | 0.033324 | 33.7571
|  | . | [5 empty] | 7 | 22 | 4 | 25.5556 | 1997-07-22 04:00 | 78 | 25.5556 | 85 | 74.3991 | 23.5551 | 75.2993 | 24.0552 | 78 | FALSE | 78 | 25.5556 | 100 | 88.0481 | 85 | 85 | 0.028393 | 28.9901 | 0.032247 | 32.6666
|  | . | [5 empty] | 7 | 22 | 5 | 25 | 1997-07-22 05:00 | 77 | 25 | 88 | 74.1616 | 23.4231 | 74.8712 | 23.8173 | 77 | FALSE | 77 | 25 | 100 | 90.4277 | 88 | 88 | 0.028215 | 28.7609 | 0.031201 | 31.607
|  | . | [5 empty] | 7 | 22 | 6 | 25 | 1997-07-22 06:00 | 77 | 25 | 91 | 74.8945 | 23.8303 | 75.4208 | 24.1227 | 77 | FALSE | 77 | 25 | 100 | 92.8274 | 91 | 91 | 0.028963 | 29.4734 | 0.031201 | 31.607
[8 empty] | 7 | 22 | 7 | 27.2222 | 1997-07-22 07:00 | 81 | 27.2222 | 82 | 76.5487 | 24.7493 | 77.6615 | 25.3675 | 81 | FALSE | 81 | 27.2222 | 100 | 85.6284 | 82 | 82 | 0.030459 | 31.1387 | 0.035571 | 36.0336
[8 empty] | 7 | 22 | 8 | 28.8889 | 1997-07-22 08:00 | 84 | 28.8889 | 77 | 78.1111 | 25.6173 | 79.5834 | 26.4352 | 84 | FALSE | 84 | 28.8889 | 100 | 81.6367 | 77 | 77 | 0.031993 | 32.7863 | 0.039189 | 39.6989
[8 empty] | 7 | 22 | 9 | 31.1111 | 1997-07-22 09:00 | 88 | 31.1111 | 70 | 79.9353 | 26.6307 | 81.9515 | 27.7508 | 88 | FALSE | 88 | 31.1111 | 100 | 76.0405 | 70 | 70 | 0.033845 | 34.8056 | 0.044509 | 45.088
[8 empty] | 7 | 22 | 10 | 32.2222 | 1997-07-22 10:00 | 90 | 32.2222 | 68 | 81.2086 | 27.3381 | 83.4064 | 28.5591 | 90 | FALSE | 90 | 32.2222 | 100 | 74.3718 | 68 | 68 | 0.03525 | 36.2785 | 0.047397 | 48.0132
[8 empty] | 7 | 22 | 11 | 33.3333 | 1997-07-22 11:00 | 92 | 33.3333 | 60 | 80.5833 | 26.9907 | 83.4375 | 28.5764 | 92 | FALSE | 92 | 33.3333 | 100 | 68.1196 | 60 | 60 | 0.034364 | 35.5485 | 0.050446 | 51.1019
[8 empty] | 7 | 22 | 12 | 33.8889 | 1997-07-22 12:00 | 93 | 33.8889 | 56 | 80.181 | 26.7672 | 83.3858 | 28.5477 | 93 | FALSE | 93 | 33.8889 | 100 | 64.9946 | 56 | 56 | 0.033819 | 35.0858 | 0.052033 | 52.7099
[8 empty] | 7 | 22 | 13 | 34.4444 | 1997-07-22 13:00 | 94 | 34.4444 | 54 | 80.392 | 26.8845 | 83.794 | 28.7745 | 94 | FALSE | 94 | 34.4444 | 100 | 63.3704 | 54 | 54 | 0.034007 | 35.3278 | 0.053664 | 54.3616
[8 empty] | 7 | 22 | 14 | 35 | 1997-07-22 14:00 | 95 | 35 | 53 | 80.9236 | 27.1798 | 84.4427 | 29.1348 | 95 | FALSE | 95 | 35 | 100 | 62.4949 | 53 | 53 | 0.034584 | 35.9442 | 0.055339 | 56.058
[8 empty] | 7 | 22 | 15 | 35 | 1997-07-22 15:00 | 95 | 35 | 49 | 79.5147 | 26.397 | 83.386 | 28.5478 | 95 | FALSE | 95 | 35 | 100 | 59.4647 | 49 | 49 | 0.032907 | 34.3306 | 0.055339 | 56.058
[8 empty] | 7 | 22 | 16 | 35.5556 | 1997-07-22 16:00 | 96 | 35.5556 | 49 | 80.3701 | 26.8723 | 84.2776 | 29.0431 | 96 | FALSE | 96 | 35.5556 | 100 | 59.332 | 49 | 49 | 0.033854 | 35.3026 | 0.057058 | 57.8001
[8 empty] | 7 | 22 | 17 | 35 | 1997-07-22 17:00 | 95 | 35 | 49 | 79.5147 | 26.397 | 83.386 | 28.5478 | 95 | FALSE | 95 | 35 | 100 | 59.4647 | 49 | 49 | 0.032907 | 34.3306 | 0.055339 | 56.058
[8 empty] | 7 | 22 | 18 | 33.8889 | 1997-07-22 18:00 | 93 | 33.8889 | 54 | 79.516 | 26.3978 | 82.887 | 28.2705 | 93 | FALSE | 93 | 33.8889 | 100 | 63.4881 | 54 | 54 | 0.033035 | 34.3321 | 0.052033 | 52.7099
[8 empty] | 7 | 22 | 19 | 32.7778 | 1997-07-22 19:00 | 91 | 32.7778 | 60 | 79.6847 | 26.4915 | 82.5135 | 28.0631 | 91 | FALSE | 91 | 32.7778 | 100 | 68.2183 | 60 | 60 | 0.033359 | 34.522 | 0.048901 | 49.5367
[8 empty] | 7 | 22 | 20 | 29.4444 | 1997-07-22 20:00 | 85 | 29.4444 | 75 | 78.5186 | 25.8437 | 80.1389 | 26.7439 | 85 | FALSE | 85 | 29.4444 | 100 | 80.048 | 75 | 75 | 0.032391 | 33.2283 | 0.040465 | 40.9907
[8 empty] | 7 | 22 | 21 | 27.7778 | 1997-07-22 21:00 | 82 | 27.7778 | 82 | 77.514 | 25.2856 | 78.6355 | 25.9086 | 82 | FALSE | 82 | 27.7778 | 100 | 85.5988 | 82 | 82 | 0.031452 | 32.1478 | 0.036743 | 37.2212
[8 empty] | 7 | 22 | 22 | 28.8889 | 1997-07-22 22:00 | 84 | 28.8889 | 77 | 78.1111 | 25.6173 | 79.5834 | 26.4352 | 84 | FALSE | 84 | 28.8889 | 100 | 81.6367 | 77 | 77 | 0.031993 | 32.7863 | 0.039189 | 39.6989
[8 empty] | 7 | 22 | 23 | 27.7778 | 1997-07-22 23:00 | 82 | 27.7778 | 82 | 77.514 | 25.2856 | 78.6355 | 25.9086 | 82 | FALSE | 82 | 27.7778 | 100 | 85.5988 | 82 | 82 | 0.031452 | 32.1478 | 0.036743 | 37.2212
[8 empty] | 7 | 22 | 24 | 27.2222 | 1997-07-23 | 81 | 27.2222 | 85 | 77.3178 | 25.1766 | 78.2384 | 25.688 | 81 | FALSE | 81 | 27.2222 | 100 | 87.9875 | 85 | 85 | 0.031298 | 31.9405 | 0.035571 | 36.0336
[8 empty] | 7 | 23 | 1 | 27.2222 | 1997-07-23 01:00 | 81 | 27.2222 | 85 | 77.3178 | 25.1766 | 78.2384 | 25.688 | 81 | FALSE | 81 | 27.2222 | 100 | 87.9875 | 85 | 85 | 0.031298 | 31.9405 | 0.035571 | 36.0336
[8 empty] | 7 | 23 | 2 | 26.6667 | 1997-07-23 02:00 | 80 | 26.6667 | 85 | 76.3449 | 24.6361 | 77.2587 | 25.1437 | 80 | FALSE | 80 | 26.6667 | 100 | 88.0077 | 85 | 85 | 0.030302 | 30.9292 | 0.034432 | 34.8792
[8 empty] | 7 | 23 | 3 | 26.6667 | 1997-07-23 03:00 | 80 | 26.6667 | 85 | 76.3449 | 24.6361 | 77.2587 | 25.1437 | 80 | FALSE | 80 | 26.6667 | 100 | 88.0077 | 85 | 85 | 0.030302 | 30.9292 | 0.034432 | 34.8792
[8 empty] | 7 | 23 | 4 | 25.5556 | 1997-07-23 04:00 | 78 | 25.5556 | 88 | 75.1419 | 23.9677 | 75.8564 | 24.3647 | 78 | FALSE | 78 | 25.5556 | 100 | 90.4168 | 88 | 88 | 0.029157 | 29.7174 | 0.032247 | 32.6666
[8 empty] | 7 | 23 | 5 | 25.5556 | 1997-07-23 05:00 | 78 | 25.5556 | 88 | 75.1419 | 23.9677 | 75.8564 | 24.3647 | 78 | FALSE | 78 | 25.5556 | 100 | 90.4168 | 88 | 88 | 0.029157 | 29.7174 | 0.032247 | 32.6666
[8 empty] | 7 | 23 | 6 | 25.5556 | 1997-07-23 06:00 | 78 | 25.5556 | 88 | 75.1419 | 23.9677 | 75.8564 | 24.3647 | 78 | FALSE | 78 | 25.5556 | 100 | 90.4168 | 88 | 88 | 0.029157 | 29.7174 | 0.032247 | 32.6666
[8 empty] | 7 | 23 | 7 | 26.6667 | 1997-07-23 07:00 | 80 | 26.6667 | 85 | 76.3449 | 24.6361 | 77.2587 | 25.1437 | 80 | FALSE | 80 | 26.6667 | 100 | 88.0077 | 85 | 85 | 0.030302 | 30.9292 | 0.034432 | 34.8792
[8 empty] | 7 | 23 | 8 | 30 | 1997-07-23 08:00 | 86 | 30 | 70 | 78.0722 | 25.5957 | 80.0541 | 26.6967 | 86 | FALSE | 86 | 30 | 100 | 76.1752 | 70 | 70 | 0.031823 | 32.7443 | 0.041776 | 42.3189
[8 empty] | 7 | 23 | 9 | 31.1111 | 1997-07-23 09:00 | 88 | 31.1111 | 65 | 78.4814 | 25.823 | 80.8611 | 27.145 | 88 | FALSE | 88 | 31.1111 | 100 | 72.2525 | 65 | 65 | 0.032159 | 33.1877 | 0.044509 | 45.088
[8 empty] | 7 | 23 | 10 | 32.7778 | 1997-07-23 10:00 | 91 | 32.7778 | 62 | 80.3078 | 26.8377 | 82.9809 | 28.3227 | 91 | FALSE | 91 | 32.7778 | 100 | 69.727 | 62 | 62 | 0.034097 | 35.231 | 0.048901 | 49.5367
[8 empty] | 7 | 23 | 11 | 33.8889 | 1997-07-23 11:00 | 93 | 33.8889 | 56 | 80.181 | 26.7672 | 83.3858 | 28.5477 | 93 | FALSE | 93 | 33.8889 | 100 | 64.9946 | 56 | 56 | 0.033819 | 35.0858 | 0.052033 | 52.7099
[8 empty] | 7 | 23 | 12 | 35 | 1997-07-23 12:00 | 95 | 35 | 53 | 80.9236 | 27.1798 | 84.4427 | 29.1348 | 95 | FALSE | 95 | 35 | 100 | 62.4949 | 53 | 53 | 0.034584 | 35.9442 | 0.055339 | 56.058
[8 empty] | 7 | 23 | 13 | 35.5556 | 1997-07-23 13:00 | 96 | 35.5556 | 49 | 80.3701 | 26.8723 | 84.2776 | 29.0431 | 96 | FALSE | 96 | 35.5556 | 100 | 59.332 | 49 | 49 | 0.033854 | 35.3026 | 0.057058 | 57.8001
[8 empty] | 7 | 23 | 14 | 36.1111 | 1997-07-23 14:00 | 97 | 36.1111 | 49 | 81.2255 | 27.3475 | 85.1691 | 29.5384 | 97 | FALSE | 97 | 36.1111 | 100 | 59.2004 | 49 | 49 | 0.034824 | 36.2985 | 0.058824 | 59.589
[8 empty] | 7 | 23 | 15 | 36.1111 | 1997-07-23 15:00 | 97 | 36.1111 | 49 | 81.2255 | 27.3475 | 85.1691 | 29.5384 | 97 | FALSE | 97 | 36.1111 | 100 | 59.2004 | 49 | 49 | 0.034824 | 36.2985 | 0.058824 | 59.589
[8 empty] | 7 | 23 | 16 | 28.3333 | 1997-07-23 16:00 | 83 | 28.3333 | 74 | 76.3582 | 24.6434 | 78.0186 | 25.5659 | 83 | FALSE | 83 | 28.3333 | 100 | 79.391 | 74 | 74 | 0.030128 | 30.9428 | 0.037949 | 38.4426
[8 empty] | 7 | 23 | 17 | 25.5556 | 1997-07-23 17:00 | 78 | 25.5556 | 88 | 75.1419 | 23.9677 | 75.8564 | 24.3647 | 78 | FALSE | 78 | 25.5556 | 100 | 90.4168 | 88 | 88 | 0.029157 | 29.7174 | 0.032247 | 32.6666
[8 empty] | 7 | 23 | 18 | 25.5556 | 1997-07-23 18:00 | 78 | 25.5556 | 88 | 75.1419 | 23.9677 | 75.8564 | 24.3647 | 78 | FALSE | 78 | 25.5556 | 100 | 90.4168 | 88 | 88 | 0.029157 | 29.7174 | 0.032247 | 32.6666
[8 empty] | 7 | 23 | 19 | 25.5556 | 1997-07-23 19:00 | 78 | 25.5556 | 85 | 74.3991 | 23.5551 | 75.2993 | 24.0552 | 78 | FALSE | 78 | 25.5556 | 100 | 88.0481 | 85 | 85 | 0.028393 | 28.9901 | 0.032247 | 32.6666
[8 empty] | 7 | 23 | 20 | 25 | 1997-07-23 20:00 | 77 | 25 | 91 | 74.8945 | 23.8303 | 75.4208 | 24.1227 | 77 | FALSE | 77 | 25 | 100 | 92.8274 | 91 | 91 | 0.028963 | 29.4734 | 0.031201 | 31.607
[8 empty] | 7 | 23 | 21 | 25.5556 | 1997-07-23 21:00 | 78 | 25.5556 | 88 | 75.1419 | 23.9677 | 75.8564 | 24.3647 | 78 | FALSE | 78 | 25.5556 | 100 | 90.4168 | 88 | 88 | 0.029157 | 29.7174 | 0.032247 | 32.6666
[8 empty] | 7 | 23 | 22 | 25.5556 | 1997-07-23 22:00 | 78 | 25.5556 | 88 | 75.1419 | 23.9677 | 75.8564 | 24.3647 | 78 | FALSE | 78 | 25.5556 | 100 | 90.4168 | 88 | 88 | 0.029157 | 29.7174 | 0.032247 | 32.6666
[8 empty] | 7 | 23 | 23 | 25 | 1997-07-23 23:00 | 77 | 25 | 91 | 74.8945 | 23.8303 | 75.4208 | 24.1227 | 77 | FALSE | 77 | 25 | 100 | 92.8274 | 91 | 91 | 0.028963 | 29.4734 | 0.031201 | 31.607
[8 empty] | 7 | 23 | 24 | 24.4444 | 1997-07-24 | 76 | 24.4444 | 94 | 74.631 | 23.6839 | 74.9733 | 23.874 | 76 | FALSE | 76 | 24.4444 | 100 | 95.2625 | 94 | 94 | 0.028755 | 29.2155 | 0.030185 | 30.5774
[8 empty] | 7 | 24 | 1 | 23.8889 | 1997-07-24 01:00 | 75 | 23.8889 | 94 | 73.6369 | 23.1316 | 73.9777 | 23.3209 | 75 | FALSE | 75 | 23.8889 | 100 | 95.2554 | 94 | 94 | 0.027812 | 28.26 | 0.029198 | 29.5773
[8 empty] | 7 | 24 | 2 | 24.4444 | 1997-07-24 02:00 | 76 | 24.4444 | 87 | 72.939 | 22.7439 | 73.7042 | 23.169 | 76 | FALSE | 76 | 24.4444 | 100 | 89.6507 | 87 | 87 | 0.027061 | 27.6055 | 0.030185 | 30.5774
[8 empty] | 7 | 24 | 3 | 24.4444 | 1997-07-24 03:00 | 76 | 24.4444 | 87 | 72.939 | 22.7439 | 73.7042 | 23.169 | 76 | FALSE | 76 | 24.4444 | 100 | 89.6507 | 87 | 87 | 0.027061 | 27.6055 | 0.030185 | 30.5774
[8 empty] | 7 | 24 | 4 | 23.8889 | 1997-07-24 04:00 | 75 | 23.8889 | 90 | 72.6805 | 22.6003 | 73.2604 | 22.9224 | 75 | FALSE | 75 | 23.8889 | 100 | 92.0323 | 90 | 90 | 0.026871 | 27.3665 | 0.029198 | 29.5773
[8 empty] | 7 | 24 | 5 | 23.3333 | 1997-07-24 05:00 | 74 | 23.3333 | 94 | 72.6428 | 22.5793 | 72.9821 | 22.7678 | 74 | FALSE | 74 | 23.3333 | 100 | 95.2482 | 94 | 94 | 0.026897 | 27.3318 | 0.028239 | 28.6058
[8 empty] | 7 | 24 | 6 | 23.3333 | 1997-07-24 06:00 | 74 | 23.3333 | 94 | 72.6428 | 22.5793 | 72.9821 | 22.7678 | 74 | FALSE | 74 | 23.3333 | 100 | 95.2482 | 94 | 94 | 0.026897 | 27.3318 | 0.028239 | 28.6058
[8 empty] | 7 | 24 | 7 | 25 | 1997-07-24 07:00 | 77 | 25 | 91 | 74.8945 | 23.8303 | 75.4208 | 24.1227 | 77 | FALSE | 77 | 25 | 100 | 92.8274 | 91 | 91 | 0.028963 | 29.4734 | 0.031201 | 31.607
[8 empty] | 7 | 24 | 8 | 26.6667 | 1997-07-24 08:00 | 80 | 26.6667 | 79 | 74.8173 | 23.7874 | 76.113 | 24.5072 | 80 | FALSE | 80 | 26.6667 | 100 | 83.3433 | 79 | 79 | 0.028696 | 29.3976 | 0.034432 | 34.8792
[8 empty] | 7 | 24 | 9 | 27.2222 | 1997-07-24 09:00 | 81 | 27.2222 | 79 | 75.7746 | 24.3192 | 77.081 | 25.045 | 81 | FALSE | 81 | 27.2222 | 100 | 83.3042 | 79 | 79 | 0.029632 | 30.3495 | 0.035571 | 36.0336
[8 empty] | 7 | 24 | 10 | 27.7778 | 1997-07-24 10:00 | 82 | 27.7778 | 79 | 76.732 | 24.8511 | 78.049 | 25.5828 | 82 | FALSE | 82 | 27.7778 | 100 | 83.2651 | 79 | 79 | 0.030594 | 31.3281 | 0.036743 | 37.2212
[8 empty] | 7 | 24 | 11 | 28.3333 | 1997-07-24 11:00 | 83 | 28.3333 | 80 | 77.9533 | 25.5296 | 79.215 | 26.2306 | 83 | FALSE | 83 | 28.3333 | 100 | 84.0035 | 80 | 80 | 0.031879 | 32.6165 | 0.037949 | 38.4426
[8 empty] | 7 | 24 | 12 | 30.5556 | 1997-07-24 12:00 | 87 | 30.5556 | 70 | 79.0037 | 26.1132 | 81.0028 | 27.2238 | 87 | FALSE | 87 | 30.5556 | 100 | 76.1077 | 70 | 70 | 0.03282 | 33.7612 | 0.043124 | 43.6844
[8 empty] | 7 | 24 | 13 | 31.6667 | 1997-07-24 13:00 | 89 | 31.6667 | 68 | 80.2832 | 26.824 | 82.4624 | 28.0347 | 89 | FALSE | 89 | 31.6667 | 100 | 74.4447 | 68 | 68 | 0.034195 | 35.2028 | 0.045934 | 46.5306
[8 empty] | 7 | 24 | 14 | 32.7778 | 1997-07-24 14:00 | 91 | 32.7778 | 62 | 80.3078 | 26.8377 | 82.9809 | 28.3227 | 91 | FALSE | 91 | 32.7778 | 100 | 69.727 | 62 | 62 | 0.034097 | 35.231 | 0.048901 | 49.5367
[8 empty] | 7 | 24 | 15 | 33.3333 | 1997-07-24 15:00 | 92 | 33.3333 | 56 | 79.2972 | 26.2762 | 82.4729 | 28.0405 | 92 | FALSE | 92 | 33.3333 | 100 | 65.1063 | 56 | 56 | 0.032844 | 34.0873 | 0.050446 | 51.1019
[8 empty] | 7 | 24 | 16 | 33.8889 | 1997-07-24 16:00 | 93 | 33.8889 | 54 | 79.516 | 26.3978 | 82.887 | 28.2705 | 93 | FALSE | 93 | 33.8889 | 100 | 63.4881 | 54 | 54 | 0.033035 | 34.3321 | 0.052033 | 52.7099
[8 empty] | 7 | 24 | 17 | 33.3333 | 1997-07-24 17:00 | 92 | 33.3333 | 58 | 79.9448 | 26.636 | 82.9586 | 28.3103 | 92 | FALSE | 92 | 33.3333 | 100 | 66.6103 | 58 | 58 | 0.033602 | 34.8164 | 0.050446 | 51.1019
[8 empty] | 7 | 24 | 18 | 32.2222 | 1997-07-24 18:00 | 90 | 32.2222 | 59 | 78.4752 | 25.8196 | 81.3564 | 27.4202 | 90 | FALSE | 90 | 32.2222 | 100 | 67.5692 | 59 | 59 | 0.032026 | 33.1809 | 0.047397 | 48.0132
[8 empty] | 7 | 24 | 19 | 30 | 1997-07-24 19:00 | 86 | 30 | 70 | 78.0722 | 25.5957 | 80.0541 | 26.6967 | 86 | FALSE | 86 | 30 | 100 | 76.1752 | 70 | 70 | 0.031823 | 32.7443 | 0.041776 | 42.3189
[8 empty] | 7 | 24 | 20 | 28.3333 | 1997-07-24 20:00 | 83 | 28.3333 | 77 | 77.1592 | 25.0885 | 78.6194 | 25.8997 | 83 | FALSE | 83 | 28.3333 | 100 | 81.6819 | 77 | 77 | 0.030998 | 31.7737 | 0.037949 | 38.4426
[8 empty] | 7 | 24 | 21 | 27.7778 | 1997-07-24 21:00 | 82 | 27.7778 | 77 | 76.2073 | 24.5596 | 77.6555 | 25.3642 | 82 | FALSE | 82 | 27.7778 | 100 | 81.7274 | 77 | 77 | 0.030029 | 30.7885 | 0.036743 | 37.2212
[8 empty] | 7 | 24 | 22 | 26.6667 | 1997-07-24 22:00 | 80 | 26.6667 | 82 | 75.5834 | 24.213 | 76.6876 | 24.8264 | 80 | FALSE | 80 | 26.6667 | 100 | 85.658 | 82 | 82 | 0.029493 | 30.1573 | 0.034432 | 34.8792
[8 empty] | 7 | 24 | 23 | 26.1111 | 1997-07-24 23:00 | 79 | 26.1111 | 88 | 76.1221 | 24.5123 | 76.8416 | 24.912 | 79 | FALSE | 79 | 26.1111 | 100 | 90.4058 | 88 | 88 | 0.030127 | 30.7016 | 0.033324 | 33.7571
[8 empty] | 7 | 24 | 24 | 25.5556 | 1997-07-25 | 78 | 25.5556 | 88 | 75.1419 | 23.9677 | 75.8564 | 24.3647 | 78 | FALSE | 78 | 25.5556 | 100 | 90.4168 | 88 | 88 | 0.029157 | 29.7174 | 0.032247 | 32.6666
[8 empty] | 7 | 25 | 1 | 25.5556 | 1997-07-25 01:00 | 78 | 25.5556 | 88 | 75.1419 | 23.9677 | 75.8564 | 24.3647 | 78 | FALSE | 78 | 25.5556 | 100 | 90.4168 | 88 | 88 | 0.029157 | 29.7174 | 0.032247 | 32.6666
[8 empty] | 7 | 25 | 2 | 24.4444 | 1997-07-25 02:00 | 76 | 24.4444 | 94 | 74.631 | 23.6839 | 74.9733 | 23.874 | 76 | FALSE | 76 | 24.4444 | 100 | 95.2625 | 94 | 94 | 0.028755 | 29.2155 | 0.030185 | 30.5774
[8 empty] | 7 | 25 | 3 | 23.3333 | 1997-07-25 03:00 | 74 | 23.3333 | 97 | 73.3521 | 22.9734 | 73.5141 | 23.0634 | 74 | FALSE | 74 | 23.3333 | 100 | 97.7091 | 97 | 97 | 0.027592 | 27.9913 | 0.028239 | 28.6058
[8 empty] | 7 | 25 | 4 | 23.3333 | 1997-07-25 04:00 | 74 | 23.3333 | 97 | 73.3521 | 22.9734 | 73.5141 | 23.0634 | 74 | FALSE | 74 | 23.3333 | 100 | 97.7091 | 97 | 97 | 0.027592 | 27.9913 | 0.028239 | 28.6058
[8 empty] | 7 | 25 | 5 | 23.8889 | 1997-07-25 05:00 | 75 | 23.8889 | 94 | 73.6369 | 23.1316 | 73.9777 | 23.3209 | 75 | FALSE | 75 | 23.8889 | 100 | 95.2554 | 94 | 94 | 0.027812 | 28.26 | 0.029198 | 29.5773
[8 empty] | 7 | 25 | 6 | 23.8889 | 1997-07-25 06:00 | 75 | 23.8889 | 94 | 73.6369 | 23.1316 | 73.9777 | 23.3209 | 75 | FALSE | 75 | 23.8889 | 100 | 95.2554 | 94 | 94 | 0.027812 | 28.26 | 0.029198 | 29.5773
[8 empty] | 7 | 25 | 7 | 25.5556 | 1997-07-25 07:00 | 78 | 25.5556 | 91 | 75.8818 | 24.3788 | 76.4113 | 24.673 | 78 | FALSE | 78 | 25.5556 | 100 | 92.8254 | 91 | 91 | 0.029934 | 30.4577 | 0.032247 | 32.6666
[8 empty] | 7 | 25 | 8 | 27.7778 | 1997-07-25 08:00 | 82 | 27.7778 | 82 | 77.514 | 25.2856 | 78.6355 | 25.9086 | 82 | FALSE | 82 | 27.7778 | 100 | 85.5988 | 82 | 82 | 0.031452 | 32.1478 | 0.036743 | 37.2212
[8 empty] | 7 | 25 | 9 | 30 | 1997-07-25 09:00 | 86 | 30 | 72 | 78.6325 | 25.9069 | 80.4744 | 26.9302 | 86 | FALSE | 86 | 30 | 100 | 77.695 | 72 | 72 | 0.032458 | 33.3527 | 0.041776 | 42.3189
[8 empty] | 7 | 25 | 10 | 31.6667 | 1997-07-25 10:00 | 89 | 31.6667 | 66 | 79.694 | 26.4967 | 82.0205 | 27.7892 | 89 | FALSE | 89 | 31.6667 | 100 | 72.9253 | 66 | 66 | 0.033497 | 34.5324 | 0.045934 | 46.5306
[8 empty] | 7 | 25 | 11 | 32.7778 | 1997-07-25 11:00 | 91 | 32.7778 | 60 | 79.6847 | 26.4915 | 82.5135 | 28.0631 | 91 | FALSE | 91 | 32.7778 | 100 | 68.2183 | 60 | 60 | 0.033359 | 34.522 | 0.048901 | 49.5367
[8 empty] | 7 | 25 | 12 | 33.3333 | 1997-07-25 12:00 | 92 | 33.3333 | 58 | 79.9448 | 26.636 | 82.9586 | 28.3103 | 92 | FALSE | 92 | 33.3333 | 100 | 66.6103 | 58 | 58 | 0.033602 | 34.8164 | 0.050446 | 51.1019
[8 empty] | 7 | 25 | 13 | 33.3333 | 1997-07-25 13:00 | 92 | 33.3333 | 58 | 79.9448 | 26.636 | 82.9586 | 28.3103 | 92 | FALSE | 92 | 33.3333 | 100 | 66.6103 | 58 | 58 | 0.033602 | 34.8164 | 0.050446 | 51.1019
[8 empty] | 7 | 25 | 14 | 34.4444 | 1997-07-25 14:00 | 94 | 34.4444 | 51 | 79.3616 | 26.312 | 83.0212 | 28.3451 | 94 | FALSE | 94 | 34.4444 | 100 | 61.106 | 51 | 51 | 0.032792 | 34.1592 | 0.053664 | 54.3616
[8 empty] | 7 | 25 | 15 | 35.5556 | 1997-07-25 15:00 | 96 | 35.5556 | 49 | 80.3701 | 26.8723 | 84.2776 | 29.0431 | 96 | FALSE | 96 | 35.5556 | 100 | 59.332 | 49 | 49 | 0.033854 | 35.3026 | 0.057058 | 57.8001
[8 empty] | 7 | 25 | 16 | 35.5556 | 1997-07-25 16:00 | 96 | 35.5556 | 48 | 80.0052 | 26.6695 | 84.0039 | 28.891 | 96 | FALSE | 96 | 35.5556 | 100 | 58.5716 | 48 | 48 | 0.03342 | 34.8851 | 0.057058 | 57.8001
[8 empty] | 7 | 25 | 17 | 35 | 1997-07-25 17:00 | 95 | 35 | 47 | 78.7899 | 25.9944 | 82.8424 | 28.2458 | 95 | FALSE | 95 | 35 | 100 | 57.9509 | 47 | 47 | 0.032069 | 33.5254 | 0.055339 | 56.058
[8 empty] | 7 | 25 | 18 | 33.8889 | 1997-07-25 18:00 | 93 | 33.8889 | 49 | 77.8038 | 25.4465 | 81.6028 | 27.5571 | 93 | FALSE | 93 | 33.8889 | 100 | 59.7337 | 49 | 49 | 0.031081 | 32.4563 | 0.052033 | 52.7099
[8 empty] | 7 | 25 | 19 | 32.2222 | 1997-07-25 19:00 | 90 | 32.2222 | 59 | 78.4752 | 25.8196 | 81.3564 | 27.4202 | 90 | FALSE | 90 | 32.2222 | 100 | 67.5692 | 59 | 59 | 0.032026 | 33.1809 | 0.047397 | 48.0132
[8 empty] | 7 | 25 | 20 | 29.4444 | 1997-07-25 20:00 | 85 | 29.4444 | 72 | 77.6949 | 25.3861 | 79.5212 | 26.4007 | 85 | FALSE | 85 | 29.4444 | 100 | 77.7562 | 72 | 72 | 0.031464 | 32.3401 | 0.040465 | 40.9907
[8 empty] | 7 | 25 | 21 | 28.8889 | 1997-07-25 21:00 | 84 | 28.8889 | 72 | 76.7573 | 24.8652 | 78.568 | 25.8711 | 84 | FALSE | 84 | 28.8889 | 100 | 77.8177 | 72 | 72 | 0.030496 | 31.3544 | 0.039189 | 39.6989
[8 empty] | 7 | 25 | 22 | 27.2222 | 1997-07-25 22:00 | 81 | 27.2222 | 79 | 75.7746 | 24.3192 | 77.081 | 25.045 | 81 | FALSE | 81 | 27.2222 | 100 | 83.3042 | 79 | 79 | 0.029632 | 30.3495 | 0.035571 | 36.0336
[8 empty] | 7 | 25 | 23 | 27.7778 | 1997-07-25 23:00 | 82 | 27.7778 | 79 | 76.732 | 24.8511 | 78.049 | 25.5828 | 82 | FALSE | 82 | 27.7778 | 100 | 83.2651 | 79 | 79 | 0.030594 | 31.3281 | 0.036743 | 37.2212
[8 empty] | 7 | 25 | 24 | 26.6667 | 1997-07-26 | 80 | 26.6667 | 85 | 76.3449 | 24.6361 | 77.2587 | 25.1437 | 80 | FALSE | 80 | 26.6667 | 100 | 88.0077 | 85 | 85 | 0.030302 | 30.9292 | 0.034432 | 34.8792
[8 empty] | 7 | 26 | 1 | 26.1111 | 1997-07-26 01:00 | 79 | 26.1111 | 88 | 76.1221 | 24.5123 | 76.8416 | 24.912 | 79 | FALSE | 79 | 26.1111 | 100 | 90.4058 | 88 | 88 | 0.030127 | 30.7016 | 0.033324 | 33.7571
[8 empty] | 7 | 26 | 2 | 25.5556 | 1997-07-26 02:00 | 78 | 25.5556 | 91 | 75.8818 | 24.3788 | 76.4113 | 24.673 | 78 | FALSE | 78 | 25.5556 | 100 | 92.8254 | 91 | 91 | 0.029934 | 30.4577 | 0.032247 | 32.6666
[8 empty] | 7 | 26 | 3 | 25 | 1997-07-26 03:00 | 77 | 25 | 91 | 74.8945 | 23.8303 | 75.4208 | 24.1227 | 77 | FALSE | 77 | 25 | 100 | 92.8274 | 91 | 91 | 0.028963 | 29.4734 | 0.031201 | 31.607
[8 empty] | 7 | 26 | 4 | 25 | 1997-07-26 04:00 | 77 | 25 | 91 | 74.8945 | 23.8303 | 75.4208 | 24.1227 | 77 | FALSE | 77 | 25 | 100 | 92.8274 | 91 | 91 | 0.028963 | 29.4734 | 0.031201 | 31.607
[8 empty] | 7 | 26 | 5 | 24.4444 | 1997-07-26 05:00 | 76 | 24.4444 | 94 | 74.631 | 23.6839 | 74.9733 | 23.874 | 76 | FALSE | 76 | 24.4444 | 100 | 95.2625 | 94 | 94 | 0.028755 | 29.2155 | 0.030185 | 30.5774
[8 empty] | 7 | 26 | 6 | 24.4444 | 1997-07-26 06:00 | 76 | 24.4444 | 94 | 74.631 | 23.6839 | 74.9733 | 23.874 | 76 | FALSE | 76 | 24.4444 | 100 | 95.2625 | 94 | 94 | 0.028755 | 29.2155 | 0.030185 | 30.5774
[8 empty] | 7 | 26 | 7 | 26.1111 | 1997-07-26 07:00 | 79 | 26.1111 | 91 | 76.8691 | 24.9273 | 77.4018 | 25.2232 | 79 | FALSE | 79 | 26.1111 | 100 | 92.8233 | 91 | 91 | 0.030932 | 31.4705 | 0.033324 | 33.7571
[8 empty] | 7 | 26 | 8 | 28.8889 | 1997-07-26 08:00 | 84 | 28.8889 | 80 | 78.9134 | 26.063 | 80.185 | 26.7695 | 84 | FALSE | 84 | 28.8889 | 100 | 83.9678 | 80 | 80 | 0.032906 | 33.6614 | 0.039189 | 39.6989
[8 empty] | 7 | 26 | 9 | 30.5556 | 1997-07-26 09:00 | 87 | 30.5556 | 72 | 79.57 | 26.4278 | 81.4275 | 27.4597 | 87 | FALSE | 87 | 30.5556 | 100 | 77.6342 | 72 | 72 | 0.033479 | 34.3928 | 0.043124 | 43.6844
[8 empty] | 7 | 26 | 10 | 32.2222 | 1997-07-26 10:00 | 90 | 32.2222 | 66 | 80.6129 | 27.0072 | 82.9597 | 28.3109 | 90 | FALSE | 90 | 32.2222 | 100 | 72.8457 | 66 | 66 | 0.034527 | 35.5829 | 0.047397 | 48.0132
[8 empty] | 7 | 26 | 11 | 33.3333 | 1997-07-26 11:00 | 92 | 33.3333 | 62 | 81.2134 | 27.3408 | 83.91 | 28.8389 | 92 | FALSE | 92 | 33.3333 | 100 | 69.6351 | 62 | 62 | 0.035128 | 36.2842 | 0.050446 | 51.1019
[8 empty] | 7 | 26 | 12 | 33.8889 | 1997-07-26 12:00 | 93 | 33.8889 | 60 | 81.4818 | 27.4899 | 84.3614 | 29.0896 | 93 | FALSE | 93 | 33.8889 | 100 | 68.0216 | 60 | 60 | 0.035394 | 36.6016 | 0.052033 | 52.7099
[8 empty] | 7 | 26 | 13 | 33.8889 | 1997-07-26 13:00 | 93 | 33.8889 | 56 | 80.181 | 26.7672 | 83.3858 | 28.5477 | 93 | FALSE | 93 | 33.8889 | 100 | 64.9946 | 56 | 56 | 0.033819 | 35.0858 | 0.052033 | 52.7099
[8 empty] | 7 | 26 | 14 | 35 | 1997-07-26 14:00 | 95 | 35 | 53 | 80.9236 | 27.1798 | 84.4427 | 29.1348 | 95 | FALSE | 95 | 35 | 100 | 62.4949 | 53 | 53 | 0.034584 | 35.9442 | 0.055339 | 56.058
[8 empty] | 7 | 26 | 15 | 35 | 1997-07-26 15:00 | 95 | 35 | 51 | 80.2255 | 26.792 | 83.9191 | 28.844 | 95 | FALSE | 95 | 35 | 100 | 60.979 | 51 | 51 | 0.033745 | 35.1367 | 0.055339 | 56.058
[8 empty] | 7 | 26 | 16 | 35.5556 | 1997-07-26 16:00 | 96 | 35.5556 | 49 | 80.3701 | 26.8723 | 84.2776 | 29.0431 | 96 | FALSE | 96 | 35.5556 | 100 | 59.332 | 49 | 49 | 0.033854 | 35.3026 | 0.057058 | 57.8001
[8 empty] | 7 | 26 | 17 | 35 | 1997-07-26 17:00 | 95 | 35 | 51 | 80.2255 | 26.792 | 83.9191 | 28.844 | 95 | FALSE | 95 | 35 | 100 | 60.979 | 51 | 51 | 0.033745 | 35.1367 | 0.055339 | 56.058
[8 empty] | 7 | 26 | 18 | 33.8889 | 1997-07-26 18:00 | 93 | 33.8889 | 56 | 80.181 | 26.7672 | 83.3858 | 28.5477 | 93 | FALSE | 93 | 33.8889 | 100 | 64.9946 | 56 | 56 | 0.033819 | 35.0858 | 0.052033 | 52.7099
[8 empty] | 7 | 26 | 19 | 32.2222 | 1997-07-26 19:00 | 90 | 32.2222 | 64 | 80.011 | 26.6728 | 82.5082 | 28.0601 | 90 | FALSE | 90 | 32.2222 | 100 | 71.3286 | 64 | 64 | 0.033808 | 34.8917 | 0.047397 | 48.0132
[8 empty] | 7 | 26 | 20 | 30 | 1997-07-26 20:00 | 86 | 30 | 70 | 78.0722 | 25.5957 | 80.0541 | 26.6967 | 86 | FALSE | 86 | 30 | 100 | 76.1752 | 70 | 70 | 0.031823 | 32.7443 | 0.041776 | 42.3189
[8 empty] | 7 | 26 | 21 | 30 | 1997-07-26 21:00 | 86 | 30 | 72 | 78.6325 | 25.9069 | 80.4744 | 26.9302 | 86 | FALSE | 86 | 30 | 100 | 77.695 | 72 | 72 | 0.032458 | 33.3527 | 0.041776 | 42.3189
[8 empty] | 7 | 26 | 22 | 29.4444 | 1997-07-26 22:00 | 85 | 29.4444 | 75 | 78.5186 | 25.8437 | 80.1389 | 26.7439 | 85 | FALSE | 85 | 29.4444 | 100 | 80.048 | 75 | 75 | 0.032391 | 33.2283 | 0.040465 | 40.9907
[8 empty] | 7 | 26 | 23 | 28.3333 | 1997-07-26 23:00 | 83 | 28.3333 | 80 | 77.9533 | 25.5296 | 79.215 | 26.2306 | 83 | FALSE | 83 | 28.3333 | 100 | 84.0035 | 80 | 80 | 0.031879 | 32.6165 | 0.037949 | 38.4426
[8 empty] | 7 | 26 | 24 | 26.6667 | 1997-07-27 | 80 | 26.6667 | 88 | 77.1024 | 25.0569 | 77.8268 | 25.4593 | 80 | FALSE | 80 | 26.6667 | 100 | 90.3947 | 88 | 88 | 0.031124 | 31.7141 | 0.034432 | 34.8792
[8 empty] | 7 | 27 | 1 | 27.2222 | 1997-07-27 01:00 | 81 | 27.2222 | 85 | 77.3178 | 25.1766 | 78.2384 | 25.688 | 81 | FALSE | 81 | 27.2222 | 100 | 87.9875 | 85 | 85 | 0.031298 | 31.9405 | 0.035571 | 36.0336
[8 empty] | 7 | 27 | 2 | 26.6667 | 1997-07-27 02:00 | 80 | 26.6667 | 85 | 76.3449 | 24.6361 | 77.2587 | 25.1437 | 80 | FALSE | 80 | 26.6667 | 100 | 88.0077 | 85 | 85 | 0.030302 | 30.9292 | 0.034432 | 34.8792
[8 empty] | 7 | 27 | 3 | 26.6667 | 1997-07-27 03:00 | 80 | 26.6667 | 85 | 76.3449 | 24.6361 | 77.2587 | 25.1437 | 80 | FALSE | 80 | 26.6667 | 100 | 88.0077 | 85 | 85 | 0.030302 | 30.9292 | 0.034432 | 34.8792
[8 empty] | 7 | 27 | 4 | 25.5556 | 1997-07-27 04:00 | 78 | 25.5556 | 91 | 75.8818 | 24.3788 | 76.4113 | 24.673 | 78 | FALSE | 78 | 25.5556 | 100 | 92.8254 | 91 | 91 | 0.029934 | 30.4577 | 0.032247 | 32.6666
[8 empty] | 7 | 27 | 5 | 25 | 1997-07-27 05:00 | 77 | 25 | 94 | 75.6252 | 24.2362 | 75.9689 | 24.4272 | 77 | FALSE | 77 | 25 | 100 | 95.2693 | 94 | 94 | 0.029725 | 30.1992 | 0.031201 | 31.607
[8 empty] | 7 | 27 | 6 | 24.4444 | 1997-07-27 06:00 | 76 | 24.4444 | 94 | 74.631 | 23.6839 | 74.9733 | 23.874 | 76 | FALSE | 76 | 24.4444 | 100 | 95.2625 | 94 | 94 | 0.028755 | 29.2155 | 0.030185 | 30.5774
[8 empty] | 7 | 27 | 7 | 27.2222 | 1997-07-27 07:00 | 81 | 27.2222 | 85 | 77.3178 | 25.1766 | 78.2384 | 25.688 | 81 | FALSE | 81 | 27.2222 | 100 | 87.9875 | 85 | 85 | 0.031298 | 31.9405 | 0.035571 | 36.0336
[8 empty] | 7 | 27 | 8 | 30 | 1997-07-27 08:00 | 86 | 30 | 75 | 79.4649 | 26.3694 | 81.0987 | 27.277 | 86 | FALSE | 86 | 30 | 100 | 79.9966 | 75 | 75 | 0.033419 | 34.2748 | 0.041776 | 42.3189
[8 empty] | 7 | 27 | 10 | 33.3333 | 1997-07-27 09:00 | 92 | 33.3333 | 62 | 81.2134 | 27.3408 | 83.91 | 28.8389 | 92 | FALSE | 92 | 33.3333 | 100 | 69.6351 | 62 | 62 | 0.035128 | 36.2842 | 0.050446 | 51.1019
[8 empty] | 7 | 27 | 11 | 33.3333 | 1997-07-27 10:00 | 92 | 33.3333 | 60 | 80.5833 | 26.9907 | 83.4375 | 28.5764 | 92 | FALSE | 92 | 33.3333 | 100 | 68.1196 | 60 | 60 | 0.034364 | 35.5485 | 0.050446 | 51.1019
[8 empty] | 7 | 27 | 12 | 34.4444 | 1997-07-27 11:00 | 94 | 34.4444 | 54 | 80.392 | 26.8845 | 83.794 | 28.7745 | 94 | FALSE | 94 | 34.4444 | 100 | 63.3704 | 54 | 54 | 0.034007 | 35.3278 | 0.053664 | 54.3616
[8 empty] | 7 | 27 | 13 | 34.4444 | 1997-07-27 12:00 | 94 | 34.4444 | 54 | 80.392 | 26.8845 | 83.794 | 28.7745 | 94 | FALSE | 94 | 34.4444 | 100 | 63.3704 | 54 | 54 | 0.034007 | 35.3278 | 0.053664 | 54.3616
[8 empty] | 7 | 27 | 14 | 36.1111 | 1997-07-27 13:00 | 97 | 36.1111 | 49 | 81.2255 | 27.3475 | 85.1691 | 29.5384 | 97 | FALSE | 97 | 36.1111 | 100 | 59.2004 | 49 | 49 | 0.034824 | 36.2985 | 0.058824 | 59.589
[8 empty] | 7 | 27 | 15 | 36.6667 | 1997-07-27 14:00 | 98 | 36.6667 | 48 | 81.7073 | 27.6152 | 85.7805 | 29.878 | 98 | FALSE | 98 | 36.6667 | 100 | 58.3029 | 48 | 48 | 0.035353 | 36.8701 | 0.060637 | 61.4256
[8 empty] | 7 | 27 | 16 | 36.6667 | 1997-07-27 15:00 | 98 | 36.6667 | 45 | 80.5625 | 26.9792 | 84.9219 | 29.4011 | 98 | FALSE | 98 | 36.6667 | 100 | 56.0007 | 45 | 45 | 0.033957 | 35.5245 | 0.060637 | 61.4256
[8 empty] | 7 | 27 | 17 | 35.5556 | 1997-07-27 16:00 | 96 | 35.5556 | 48 | 80.0052 | 26.6695 | 84.0039 | 28.891 | 96 | FALSE | 96 | 35.5556 | 100 | 58.5716 | 48 | 48 | 0.03342 | 34.8851 | 0.057058 | 57.8001
[8 empty] | 7 | 27 | 18 | 35 | 1997-07-27 17:00 | 95 | 35 | 51 | 80.2255 | 26.792 | 83.9191 | 28.844 | 95 | FALSE | 95 | 35 | 100 | 60.979 | 51 | 51 | 0.033745 | 35.1367 | 0.055339 | 56.058
[8 empty] | 7 | 27 | 19 | 33.3333 | 1997-07-27 18:00 | 92 | 33.3333 | 58 | 79.9448 | 26.636 | 82.9586 | 28.3103 | 92 | FALSE | 92 | 33.3333 | 100 | 66.6103 | 58 | 58 | 0.033602 | 34.8164 | 0.050446 | 51.1019
[8 empty] | 7 | 27 | 20 | 30.5556 | 1997-07-27 19:00 | 87 | 30.5556 | 70 | 79.0037 | 26.1132 | 81.0028 | 27.2238 | 87 | FALSE | 87 | 30.5556 | 100 | 76.1077 | 70 | 70 | 0.03282 | 33.7612 | 0.043124 | 43.6844
[8 empty] | 7 | 27 | 21 | 30 | 1997-07-27 20:00 | 86 | 30 | 70 | 78.0722 | 25.5957 | 80.0541 | 26.6967 | 86 | FALSE | 86 | 30 | 100 | 76.1752 | 70 | 70 | 0.031823 | 32.7443 | 0.041776 | 42.3189
[8 empty] | 7 | 27 | 22 | 30 | 1997-07-27 21:00 | 86 | 30 | 72 | 78.6325 | 25.9069 | 80.4744 | 26.9302 | 86 | FALSE | 86 | 30 | 100 | 77.695 | 72 | 72 | 0.032458 | 33.3527 | 0.041776 | 42.3189
[8 empty] | 7 | 27 | 23 | 28.3333 | 1997-07-27 22:00 | 83 | 28.3333 | 80 | 77.9533 | 25.5296 | 79.215 | 26.2306 | 83 | FALSE | 83 | 28.3333 | 100 | 84.0035 | 80 | 80 | 0.031879 | 32.6165 | 0.037949 | 38.4426
[8 empty] | 7 | 27 | 24 | 28.8889 | 1997-07-27 23:00 | 84 | 28.8889 | 80 | 78.9134 | 26.063 | 80.185 | 26.7695 | 84 | FALSE | 84 | 28.8889 | 100 | 83.9678 | 80 | 80 | 0.032906 | 33.6614 | 0.039189 | 39.6989
[8 empty] | 7 | 28 | 1 | 28.3333 | 1997-07-28 | 83 | 28.3333 | 80 | 77.9533 | 25.5296 | 79.215 | 26.2306 | 83 | FALSE | 83 | 28.3333 | 100 | 84.0035 | 80 | 80 | 0.031879 | 32.6165 | 0.037949 | 38.4426
[8 empty] | 7 | 28 | 2 | 27.2222 | 1997-07-28 01:00 | 81 | 27.2222 | 85 | 77.3178 | 25.1766 | 78.2384 | 25.688 | 81 | FALSE | 81 | 27.2222 | 100 | 87.9875 | 85 | 85 | 0.031298 | 31.9405 | 0.035571 | 36.0336
[8 empty] | 7 | 28 | 3 | 26.6667 | 1997-07-28 02:00 | 80 | 26.6667 | 88 | 77.1024 | 25.0569 | 77.8268 | 25.4593 | 80 | FALSE | 80 | 26.6667 | 100 | 90.3947 | 88 | 88 | 0.031124 | 31.7141 | 0.034432 | 34.8792
[8 empty] | 7 | 28 | 4 | 26.6667 | 1997-07-28 03:00 | 80 | 26.6667 | 85 | 76.3449 | 24.6361 | 77.2587 | 25.1437 | 80 | FALSE | 80 | 26.6667 | 100 | 88.0077 | 85 | 85 | 0.030302 | 30.9292 | 0.034432 | 34.8792
[8 empty] | 7 | 28 | 5 | 25.5556 | 1997-07-28 04:00 | 78 | 25.5556 | 91 | 75.8818 | 24.3788 | 76.4113 | 24.673 | 78 | FALSE | 78 | 25.5556 | 100 | 92.8254 | 91 | 91 | 0.029934 | 30.4577 | 0.032247 | 32.6666
[8 empty] | 7 | 28 | 6 | 25.5556 | 1997-07-28 05:00 | 78 | 25.5556 | 94 | 76.6193 | 24.7885 | 76.9645 | 24.9803 | 78 | FALSE | 78 | 25.5556 | 100 | 95.276 | 94 | 94 | 0.030724 | 31.2115 | 0.032247 | 32.6666
[8 empty] | 7 | 28 | 7 | 27.7778 | 1997-07-28 06:00 | 82 | 27.7778 | 85 | 78.2907 | 25.7171 | 79.218 | 26.2322 | 82 | FALSE | 82 | 27.7778 | 100 | 87.9672 | 85 | 85 | 0.032322 | 32.9804 | 0.036743 | 37.2212
[8 empty] | 7 | 28 | 8 | 30 | 1997-07-28 07:00 | 86 | 30 | 77 | 80.0149 | 26.675 | 81.5112 | 27.5062 | 86 | FALSE | 86 | 30 | 100 | 81.5466 | 77 | 77 | 0.034067 | 34.8962 | 0.041776 | 42.3189
[8 empty] | 7 | 28 | 9 | 31.6667 | 1997-07-28 08:00 | 89 | 31.6667 | 68 | 80.2832 | 26.824 | 82.4624 | 28.0347 | 89 | FALSE | 89 | 31.6667 | 100 | 74.4447 | 68 | 68 | 0.034195 | 35.2028 | 0.045934 | 46.5306
[8 empty] | 7 | 28 | 10 | 33.3333 | 1997-07-28 09:00 | 92 | 33.3333 | 60 | 80.5833 | 26.9907 | 83.4375 | 28.5764 | 92 | FALSE | 92 | 33.3333 | 100 | 68.1196 | 60 | 60 | 0.034364 | 35.5485 | 0.050446 | 51.1019
[8 empty] | 7 | 28 | 11 | 34.4444 | 1997-07-28 10:00 | 94 | 34.4444 | 54 | 80.392 | 26.8845 | 83.794 | 28.7745 | 94 | FALSE | 94 | 34.4444 | 100 | 63.3704 | 54 | 54 | 0.034007 | 35.3278 | 0.053664 | 54.3616
[8 empty] | 7 | 28 | 12 | 35 | 1997-07-28 11:00 | 95 | 35 | 49 | 79.5147 | 26.397 | 83.386 | 28.5478 | 95 | FALSE | 95 | 35 | 100 | 59.4647 | 49 | 49 | 0.032907 | 34.3306 | 0.055339 | 56.058
[8 empty] | 7 | 28 | 13 | 34.4444 | 1997-07-28 12:00 | 94 | 34.4444 | 51 | 79.3616 | 26.312 | 83.0212 | 28.3451 | 94 | FALSE | 94 | 34.4444 | 100 | 61.106 | 51 | 51 | 0.032792 | 34.1592 | 0.053664 | 54.3616
[8 empty] | 7 | 28 | 14 | 36.1111 | 1997-07-28 13:00 | 97 | 36.1111 | 42 | 78.5553 | 25.864 | 83.1664 | 28.4258 | 97 | FALSE | 97 | 36.1111 | 100 | 53.8479 | 42 | 42 | 0.031676 | 33.2683 | 0.058824 | 59.589
[8 empty] | 7 | 28 | 15 | 36.1111 | 1997-07-28 14:00 | 97 | 36.1111 | 42 | 78.5553 | 25.864 | 83.1664 | 28.4258 | 97 | FALSE | 97 | 36.1111 | 100 | 53.8479 | 42 | 42 | 0.031676 | 33.2683 | 0.058824 | 59.589
[8 empty] | 7 | 28 | 16 | 36.1111 | 1997-07-28 15:00 | 97 | 36.1111 | 43 | 78.9498 | 26.0832 | 83.4623 | 28.5902 | 97 | FALSE | 97 | 36.1111 | 100 | 54.6143 | 43 | 43 | 0.032126 | 33.7016 | 0.058824 | 59.589
[8 empty] | 7 | 28 | 17 | 35 | 1997-07-28 16:00 | 95 | 35 | 46 | 78.4219 | 25.79 | 82.5665 | 28.0925 | 95 | FALSE | 95 | 35 | 100 | 57.1938 | 46 | 46 | 0.03165 | 33.1229 | 0.055339 | 56.058
[8 empty] | 7 | 28 | 18 | 34.4444 | 1997-07-28 17:00 | 94 | 34.4444 | 49 | 78.6592 | 25.9218 | 82.4944 | 28.0525 | 94 | FALSE | 94 | 34.4444 | 100 | 59.5986 | 49 | 49 | 0.031983 | 33.382 | 0.053664 | 54.3616
[8 empty] | 7 | 28 | 19 | 32.7778 | 1997-07-28 18:00 | 91 | 32.7778 | 56 | 78.4134 | 25.7852 | 81.5601 | 27.5334 | 91 | FALSE | 91 | 32.7778 | 100 | 65.2188 | 56 | 56 | 0.031893 | 33.1137 | 0.048901 | 49.5367
[8 empty] | 7 | 28 | 20 | 30 | 1997-07-28 19:00 | 86 | 30 | 68 | 77.5072 | 25.2818 | 79.6304 | 26.4613 | 86 | FALSE | 86 | 30 | 100 | 74.6661 | 68 | 68 | 0.031192 | 32.1406 | 0.041776 | 42.3189
[8 empty] | 7 | 28 | 21 | 30 | 1997-07-28 20:00 | 86 | 30 | 65 | 76.65 | 24.8056 | 78.9875 | 26.1042 | 86 | FALSE | 86 | 30 | 100 | 72.4211 | 65 | 65 | 0.030255 | 31.2433 | 0.041776 | 42.3189
[8 empty] | 7 | 28 | 22 | 28.8889 | 1997-07-28 21:00 | 84 | 28.8889 | 70 | 76.2091 | 24.5606 | 78.1568 | 25.6427 | 84 | FALSE | 84 | 28.8889 | 100 | 76.3113 | 70 | 70 | 0.029906 | 30.7903 | 0.039189 | 39.6989
[8 empty] | 7 | 28 | 23 | 28.3333 | 1997-07-28 22:00 | 83 | 28.3333 | 72 | 75.8198 | 24.3443 | 77.6148 | 25.3416 | 83 | FALSE | 83 | 28.3333 | 100 | 77.8795 | 72 | 72 | 0.029555 | 30.395 | 0.037949 | 38.4426
[8 empty] | 7 | 28 | 24 | 27.2222 | 1997-07-28 23:00 | 81 | 27.2222 | 77 | 75.2554 | 24.0308 | 76.6916 | 24.8287 | 81 | FALSE | 81 | 27.2222 | 100 | 81.773 | 77 | 77 | 0.029088 | 29.83 | 0.035571 | 36.0336
[8 empty] | 7 | 29 | 1 | 27.7778 | 1997-07-29 | 82 | 27.7778 | 74 | 75.4148 | 24.1193 | 77.0611 | 25.0339 | 82 | FALSE | 82 | 27.7778 | 100 | 79.4463 | 74 | 74 | 0.029191 | 29.9886 | 0.036743 | 37.2212
[8 empty] | 7 | 29 | 2 | 26.6667 | 1997-07-29 01:00 | 80 | 26.6667 | 79 | 74.8173 | 23.7874 | 76.113 | 24.5072 | 80 | FALSE | 80 | 26.6667 | 100 | 83.3433 | 79 | 79 | 0.028696 | 29.3976 | 0.034432 | 34.8792
[8 empty] | 7 | 29 | 3 | 25 | 1997-07-29 02:00 | 77 | 25 | 88 | 74.1616 | 23.4231 | 74.8712 | 23.8173 | 77 | FALSE | 77 | 25 | 100 | 90.4277 | 88 | 88 | 0.028215 | 28.7609 | 0.031201 | 31.607
[8 empty] | 7 | 29 | 4 | 25.5556 | 1997-07-29 03:00 | 78 | 25.5556 | 85 | 74.3991 | 23.5551 | 75.2993 | 24.0552 | 78 | FALSE | 78 | 25.5556 | 100 | 88.0481 | 85 | 85 | 0.028393 | 28.9901 | 0.032247 | 32.6666
[8 empty] | 7 | 29 | 5 | 26.1111 | 1997-07-29 04:00 | 79 | 26.1111 | 82 | 74.6181 | 23.6767 | 75.7136 | 24.2853 | 79 | FALSE | 79 | 26.1111 | 100 | 85.6876 | 82 | 82 | 0.028554 | 29.203 | 0.033324 | 33.7571
[8 empty] | 7 | 29 | 6 | 24.4444 | 1997-07-29 05:00 | 76 | 24.4444 | 90 | 73.6655 | 23.1475 | 74.2491 | 23.4717 | 76 | FALSE | 76 | 24.4444 | 100 | 92.0277 | 90 | 90 | 0.027779 | 28.287 | 0.030185 | 30.5774
[8 empty] | 7 | 29 | 7 | 26.6667 | 1997-07-29 06:00 | 80 | 26.6667 | 82 | 75.5834 | 24.213 | 76.6876 | 24.8264 | 80 | FALSE | 80 | 26.6667 | 100 | 85.658 | 82 | 82 | 0.029493 | 30.1573 | 0.034432 | 34.8792
[8 empty] | 7 | 29 | 8 | 28.3333 | 1997-07-29 07:00 | 83 | 28.3333 | 77 | 77.1592 | 25.0885 | 78.6194 | 25.8997 | 83 | FALSE | 83 | 28.3333 | 100 | 81.6819 | 77 | 77 | 0.030998 | 31.7737 | 0.037949 | 38.4426
[8 empty] | 7 | 29 | 9 | 31.6667 | 1997-07-29 08:00 | 89 | 31.6667 | 63 | 78.7985 | 25.9992 | 81.3489 | 27.416 | 89 | FALSE | 89 | 31.6667 | 100 | 70.6628 | 63 | 63 | 0.032458 | 33.5349 | 0.045934 | 46.5306
[8 empty] | 7 | 29 | 10 | 32.7778 | 1997-07-29 09:00 | 91 | 32.7778 | 60 | 79.6847 | 26.4915 | 82.5135 | 28.0631 | 91 | FALSE | 91 | 32.7778 | 100 | 68.2183 | 60 | 60 | 0.033359 | 34.522 | 0.048901 | 49.5367
[8 empty] | 7 | 29 | 11 | 33.8889 | 1997-07-29 10:00 | 93 | 33.8889 | 54 | 79.516 | 26.3978 | 82.887 | 28.2705 | 93 | FALSE | 93 | 33.8889 | 100 | 63.4881 | 54 | 54 | 0.033035 | 34.3321 | 0.052033 | 52.7099
[8 empty] | 7 | 29 | 12 | 34.4444 | 1997-07-29 11:00 | 94 | 34.4444 | 51 | 79.3616 | 26.312 | 83.0212 | 28.3451 | 94 | FALSE | 94 | 34.4444 | 100 | 61.106 | 51 | 51 | 0.032792 | 34.1592 | 0.053664 | 54.3616
[8 empty] | 7 | 29 | 13 | 35 | 1997-07-29 12:00 | 95 | 35 | 47 | 78.7899 | 25.9944 | 82.8424 | 28.2458 | 95 | FALSE | 95 | 35 | 100 | 57.9509 | 47 | 47 | 0.032069 | 33.5254 | 0.055339 | 56.058
[8 empty] | 7 | 29 | 14 | 35.5556 | 1997-07-29 13:00 | 96 | 35.5556 | 48 | 80.0052 | 26.6695 | 84.0039 | 28.891 | 96 | FALSE | 96 | 35.5556 | 100 | 58.5716 | 48 | 48 | 0.03342 | 34.8851 | 0.057058 | 57.8001
[8 empty] | 7 | 29 | 15 | 36.1111 | 1997-07-29 14:00 | 97 | 36.1111 | 46 | 80.1062 | 26.7256 | 84.3296 | 29.072 | 97 | FALSE | 97 | 36.1111 | 100 | 56.9089 | 46 | 46 | 0.033476 | 35.0002 | 0.058824 | 59.589
[8 empty] | 7 | 29 | 16 | 36.6667 | 1997-07-29 15:00 | 98 | 36.6667 | 43 | 79.7778 | 26.5432 | 84.3333 | 29.0741 | 98 | FALSE | 98 | 36.6667 | 100 | 54.4637 | 43 | 43 | 0.033025 | 34.627 | 0.060637 | 61.4256
[8 empty] | 7 | 29 | 17 | 36.1111 | 1997-07-29 16:00 | 97 | 36.1111 | 46 | 80.1062 | 26.7256 | 84.3296 | 29.072 | 97 | FALSE | 97 | 36.1111 | 100 | 56.9089 | 46 | 46 | 0.033476 | 35.0002 | 0.058824 | 59.589
[8 empty] | 7 | 29 | 18 | 32.7778 | 1997-07-29 17:00 | 91 | 32.7778 | 60 | 79.6847 | 26.4915 | 82.5135 | 28.0631 | 91 | FALSE | 91 | 32.7778 | 100 | 68.2183 | 60 | 60 | 0.033359 | 34.522 | 0.048901 | 49.5367
[8 empty] | 7 | 29 | 19 | 29.4444 | 1997-07-29 18:00 | 85 | 29.4444 | 70 | 77.1406 | 25.0781 | 79.1055 | 26.1697 | 85 | FALSE | 85 | 29.4444 | 100 | 76.2431 | 70 | 70 | 0.030851 | 31.7542 | 0.040465 | 40.9907
[8 empty] | 7 | 29 | 20 | 27.7778 | 1997-07-29 19:00 | 82 | 27.7778 | 74 | 75.4148 | 24.1193 | 77.0611 | 25.0339 | 82 | FALSE | 82 | 27.7778 | 100 | 79.4463 | 74 | 74 | 0.029191 | 29.9886 | 0.036743 | 37.2212
[8 empty] | 7 | 29 | 21 | 27.2222 | 1997-07-29 20:00 | 81 | 27.2222 | 77 | 75.2554 | 24.0308 | 76.6916 | 24.8287 | 81 | FALSE | 81 | 27.2222 | 100 | 81.773 | 77 | 77 | 0.029088 | 29.83 | 0.035571 | 36.0336
[8 empty] | 7 | 29 | 22 | 26.1111 | 1997-07-29 21:00 | 79 | 26.1111 | 82 | 74.6181 | 23.6767 | 75.7136 | 24.2853 | 79 | FALSE | 79 | 26.1111 | 100 | 85.6876 | 82 | 82 | 0.028554 | 29.203 | 0.033324 | 33.7571
[8 empty] | 7 | 29 | 23 | 25.5556 | 1997-07-29 22:00 | 78 | 25.5556 | 85 | 74.3991 | 23.5551 | 75.2993 | 24.0552 | 78 | FALSE | 78 | 25.5556 | 100 | 88.0481 | 85 | 85 | 0.028393 | 28.9901 | 0.032247 | 32.6666
[8 empty] | 7 | 29 | 24 | 25.5556 | 1997-07-29 23:00 | 78 | 25.5556 | 85 | 74.3991 | 23.5551 | 75.2993 | 24.0552 | 78 | FALSE | 78 | 25.5556 | 100 | 88.0481 | 85 | 85 | 0.028393 | 28.9901 | 0.032247 | 32.6666
[8 empty] | 7 | 30 | 1 | 25 | 1997-07-30 | 77 | 25 | 88 | 74.1616 | 23.4231 | 74.8712 | 23.8173 | 77 | FALSE | 77 | 25 | 100 | 90.4277 | 88 | 88 | 0.028215 | 28.7609 | 0.031201 | 31.607
[8 empty] | 7 | 30 | 2 | 25.5556 | 1997-07-30 01:00 | 78 | 25.5556 | 85 | 74.3991 | 23.5551 | 75.2993 | 24.0552 | 78 | FALSE | 78 | 25.5556 | 100 | 88.0481 | 85 | 85 | 0.028393 | 28.9901 | 0.032247 | 32.6666
[8 empty] | 7 | 30 | 3 | 25 | 1997-07-30 02:00 | 77 | 25 | 91 | 74.8945 | 23.8303 | 75.4208 | 24.1227 | 77 | FALSE | 77 | 25 | 100 | 92.8274 | 91 | 91 | 0.028963 | 29.4734 | 0.031201 | 31.607
[8 empty] | 7 | 30 | 4 | 24.4444 | 1997-07-30 03:00 | 76 | 24.4444 | 94 | 74.631 | 23.6839 | 74.9733 | 23.874 | 76 | FALSE | 76 | 24.4444 | 100 | 95.2625 | 94 | 94 | 0.028755 | 29.2155 | 0.030185 | 30.5774
[8 empty] | 7 | 30 | 5 | 24.4444 | 1997-07-30 04:00 | 76 | 24.4444 | 90 | 73.6655 | 23.1475 | 74.2491 | 23.4717 | 76 | FALSE | 76 | 24.4444 | 100 | 92.0277 | 90 | 90 | 0.027779 | 28.287 | 0.030185 | 30.5774
[8 empty] | 7 | 30 | 6 | 25 | 1997-07-30 05:00 | 77 | 25 | 88 | 74.1616 | 23.4231 | 74.8712 | 23.8173 | 77 | FALSE | 77 | 25 | 100 | 90.4277 | 88 | 88 | 0.028215 | 28.7609 | 0.031201 | 31.607
[8 empty] | 7 | 30 | 7 | 26.1111 | 1997-07-30 06:00 | 79 | 26.1111 | 85 | 75.372 | 24.0956 | 76.279 | 24.5994 | 79 | FALSE | 79 | 26.1111 | 100 | 88.0279 | 85 | 85 | 0.029334 | 29.946 | 0.033324 | 33.7571
[8 empty] | 7 | 30 | 8 | 27.2222 | 1997-07-30 07:00 | 81 | 27.2222 | 82 | 76.5487 | 24.7493 | 77.6615 | 25.3675 | 81 | FALSE | 81 | 27.2222 | 100 | 85.6284 | 82 | 82 | 0.030459 | 31.1387 | 0.035571 | 36.0336
[8 empty] | 7 | 30 | 9 | 27.2222 | 1997-07-30 08:00 | 81 | 27.2222 | 82 | 76.5487 | 24.7493 | 77.6615 | 25.3675 | 81 | FALSE | 81 | 27.2222 | 100 | 85.6284 | 82 | 82 | 0.030459 | 31.1387 | 0.035571 | 36.0336
[8 empty] | 7 | 30 | 10 | 27.2222 | 1997-07-30 09:00 | 81 | 27.2222 | 82 | 76.5487 | 24.7493 | 77.6615 | 25.3675 | 81 | FALSE | 81 | 27.2222 | 100 | 85.6284 | 82 | 82 | 0.030459 | 31.1387 | 0.035571 | 36.0336
[8 empty] | 7 | 30 | 11 | 28.3333 | 1997-07-30 10:00 | 83 | 28.3333 | 77 | 77.1592 | 25.0885 | 78.6194 | 25.8997 | 83 | FALSE | 83 | 28.3333 | 100 | 81.6819 | 77 | 77 | 0.030998 | 31.7737 | 0.037949 | 38.4426
[8 empty] | 7 | 30 | 12 | 28.8889 | 1997-07-30 11:00 | 84 | 28.8889 | 74 | 77.3016 | 25.1676 | 78.9762 | 26.0979 | 84 | FALSE | 84 | 28.8889 | 100 | 79.3359 | 74 | 74 | 0.031091 | 31.9234 | 0.039189 | 39.6989
[8 empty] | 7 | 30 | 13 | 29.4444 | 1997-07-30 12:00 | 85 | 29.4444 | 72 | 77.6949 | 25.3861 | 79.5212 | 26.4007 | 85 | FALSE | 85 | 29.4444 | 100 | 77.7562 | 72 | 72 | 0.031464 | 32.3401 | 0.040465 | 40.9907
[8 empty] | 7 | 30 | 14 | 26.6667 | 1997-07-30 13:00 | 80 | 26.6667 | 91 | 77.8564 | 25.4758 | 78.3923 | 25.7735 | 80 | FALSE | 80 | 26.6667 | 100 | 92.821 | 91 | 91 | 0.03196 | 32.5126 | 0.034432 | 34.8792
[8 empty] | 7 | 30 | 15 | 27.7778 | 1997-07-30 14:00 | 82 | 27.7778 | 82 | 77.514 | 25.2856 | 78.6355 | 25.9086 | 82 | FALSE | 82 | 27.7778 | 100 | 85.5988 | 82 | 82 | 0.031452 | 32.1478 | 0.036743 | 37.2212
[8 empty] | 7 | 30 | 16 | 29.4444 | 1997-07-30 15:00 | 85 | 29.4444 | 70 | 77.1406 | 25.0781 | 79.1055 | 26.1697 | 85 | FALSE | 85 | 29.4444 | 100 | 76.2431 | 70 | 70 | 0.030851 | 31.7542 | 0.040465 | 40.9907
[8 empty] | 7 | 30 | 17 | 29.4444 | 1997-07-30 16:00 | 85 | 29.4444 | 70 | 77.1406 | 25.0781 | 79.1055 | 26.1697 | 85 | FALSE | 85 | 29.4444 | 100 | 76.2431 | 70 | 70 | 0.030851 | 31.7542 | 0.040465 | 40.9907
[8 empty] | 7 | 30 | 18 | 29.4444 | 1997-07-30 17:00 | 85 | 29.4444 | 70 | 77.1406 | 25.0781 | 79.1055 | 26.1697 | 85 | FALSE | 85 | 29.4444 | 100 | 76.2431 | 70 | 70 | 0.030851 | 31.7542 | 0.040465 | 40.9907
[8 empty] | 7 | 30 | 19 | 28.3333 | 1997-07-30 18:00 | 83 | 28.3333 | 72 | 75.8198 | 24.3443 | 77.6148 | 25.3416 | 83 | FALSE | 83 | 28.3333 | 100 | 77.8795 | 72 | 72 | 0.029555 | 30.395 | 0.037949 | 38.4426
[8 empty] | 7 | 30 | 20 | 26.6667 | 1997-07-30 19:00 | 80 | 26.6667 | 79 | 74.8173 | 23.7874 | 76.113 | 24.5072 | 80 | FALSE | 80 | 26.6667 | 100 | 83.3433 | 79 | 79 | 0.028696 | 29.3976 | 0.034432 | 34.8792
[8 empty] | 7 | 30 | 21 | 27.7778 | 1997-07-30 20:00 | 82 | 27.7778 | 74 | 75.4148 | 24.1193 | 77.0611 | 25.0339 | 82 | FALSE | 82 | 27.7778 | 100 | 79.4463 | 74 | 74 | 0.029191 | 29.9886 | 0.036743 | 37.2212
[8 empty] | 7 | 30 | 22 | 27.2222 | 1997-07-30 21:00 | 81 | 27.2222 | 77 | 75.2554 | 24.0308 | 76.6916 | 24.8287 | 81 | FALSE | 81 | 27.2222 | 100 | 81.773 | 77 | 77 | 0.029088 | 29.83 | 0.035571 | 36.0336
[8 empty] | 7 | 30 | 23 | 27.2222 | 1997-07-30 22:00 | 81 | 27.2222 | 77 | 75.2554 | 24.0308 | 76.6916 | 24.8287 | 81 | FALSE | 81 | 27.2222 | 100 | 81.773 | 77 | 77 | 0.029088 | 29.83 | 0.035571 | 36.0336
[8 empty] | 7 | 30 | 24 | 26.6667 | 1997-07-30 23:00 | 80 | 26.6667 | 77 | 74.3035 | 23.502 | 75.7277 | 24.2931 | 80 | FALSE | 80 | 26.6667 | 100 | 81.8187 | 77 | 77 | 0.028171 | 28.8977 | 0.034432 | 34.8792
[8 empty] | 7 | 31 | 1 | 26.1111 | 1997-07-31 | 79 | 26.1111 | 77 | 73.3516 | 22.9731 | 74.7637 | 23.7576 | 79 | FALSE | 79 | 26.1111 | 100 | 81.8646 | 77 | 77 | 0.02728 | 27.9909 | 0.033324 | 33.7571
[8 empty] | 7 | 31 | 2 | 26.1111 | 1997-07-31 01:00 | 79 | 26.1111 | 74 | 72.5845 | 22.5469 | 74.1884 | 23.438 | 79 | FALSE | 79 | 26.1111 | 100 | 79.6137 | 74 | 74 | 0.02653 | 27.2782 | 0.033324 | 33.7571
[8 empty] | 7 | 31 | 3 | 25.5556 | 1997-07-31 02:00 | 78 | 25.5556 | 77 | 72.3997 | 22.4443 | 73.7998 | 23.2221 | 78 | FALSE | 78 | 25.5556 | 100 | 81.9106 | 77 | 77 | 0.026414 | 27.109 | 0.032247 | 32.6666
[8 empty] | 7 | 31 | 4 | 25 | 1997-07-31 03:00 | 77 | 25 | 79 | 71.9452 | 22.1918 | 73.2089 | 22.8938 | 77 | FALSE | 77 | 25 | 100 | 83.4614 | 79 | 79 | 0.026041 | 26.6965 | 0.031201 | 31.607
[8 empty] | 7 | 31 | 5 | 24.4444 | 1997-07-31 04:00 | 76 | 24.4444 | 79 | 70.9878 | 21.6599 | 72.2409 | 22.356 | 76 | FALSE | 76 | 24.4444 | 100 | 83.5009 | 79 | 79 | 0.025205 | 25.8457 | 0.030185 | 30.5774
[8 empty] | 7 | 31 | 6 | 23.8889 | 1997-07-31 05:00 | 75 | 23.8889 | 82 | 70.757 | 21.5317 | 71.8177 | 22.121 | 75 | FALSE | 75 | 23.8889 | 100 | 85.806 | 82 | 82 | 0.025053 | 25.6441 | 0.029198 | 29.5773
[8 empty] | 7 | 31 | 7 | 23.8889 | 1997-07-31 06:00 | 75 | 23.8889 | 79 | 70.0305 | 21.128 | 71.2728 | 21.8182 | 75 | FALSE | 75 | 23.8889 | 100 | 83.5404 | 79 | 79 | 0.024392 | 25.0186 | 0.029198 | 29.5773
[8 empty] | 7 | 31 | 8 | 25 | 1997-07-31 07:00 | 77 | 25 | 76 | 71.1984 | 21.7769 | 72.6488 | 22.5826 | 77 | FALSE | 77 | 25 | 100 | 81.2098 | 76 | 76 | 0.025339 | 26.0307 | 0.031201 | 31.607
[8 empty] | 7 | 31 | 9 | 26.6667 | 1997-07-31 08:00 | 80 | 26.6667 | 72 | 73.0071 | 22.7817 | 74.7553 | 23.7529 | 80 | FALSE | 80 | 26.6667 | 100 | 78.0667 | 72 | 72 | 0.02688 | 27.6688 | 0.034432 | 34.8792
[8 empty] | 7 | 31 | 10 | 28.3333 | 1997-07-31 09:00 | 83 | 28.3333 | 70 | 75.2776 | 24.0431 | 77.2082 | 25.1156 | 83 | FALSE | 83 | 28.3333 | 100 | 76.3799 | 70 | 70 | 0.028986 | 29.852 | 0.037949 | 38.4426
[8 empty] | 7 | 31 | 11 | 30 | 1997-07-31 10:00 | 86 | 30 | 65 | 76.65 | 24.8056 | 78.9875 | 26.1042 | 86 | FALSE | 86 | 30 | 100 | 72.4211 | 65 | 65 | 0.030255 | 31.2433 | 0.041776 | 42.3189
[8 empty] | 7 | 31 | 12 | 31.6667 | 1997-07-31 11:00 | 89 | 31.6667 | 59 | 77.5802 | 25.3224 | 80.4352 | 26.9084 | 89 | FALSE | 89 | 31.6667 | 100 | 67.6728 | 59 | 59 | 0.031084 | 32.2181 | 0.045934 | 46.5306
[8 empty] | 7 | 31 | 13 | 32.2222 | 1997-07-31 12:00 | 90 | 32.2222 | 54 | 76.8878 | 24.9376 | 80.1658 | 26.7588 | 90 | FALSE | 90 | 32.2222 | 100 | 63.8467 | 54 | 54 | 0.030261 | 31.49 | 0.047397 | 48.0132
[8 empty] | 7 | 31 | 14 | 33.3333 | 1997-07-31 13:00 | 92 | 33.3333 | 49 | 76.9484 | 24.9713 | 80.7113 | 27.0618 | 92 | FALSE | 92 | 33.3333 | 100 | 59.87 | 49 | 49 | 0.030202 | 31.5531 | 0.050446 | 51.1019
[8 empty] | 7 | 31 | 15 | 32.7778 | 1997-07-31 14:00 | 91 | 32.7778 | 49 | 76.0929 | 24.4961 | 79.8197 | 26.5665 | 91 | FALSE | 91 | 32.7778 | 100 | 60.0074 | 49 | 49 | 0.029344 | 30.6719 | 0.048901 | 49.5367
[8 empty] | 7 | 31 | 16 | 32.7778 | 1997-07-31 15:00 | 91 | 32.7778 | 45 | 74.7 | 23.7222 | 78.775 | 25.9861 | 91 | FALSE | 91 | 32.7778 | 100 | 57.0363 | 45 | 45 | 0.027891 | 29.2829 | 0.048901 | 49.5367
[8 empty] | 7 | 31 | 17 | 32.2222 | 1997-07-31 16:00 | 90 | 32.2222 | 45 | 73.8625 | 23.257 | 77.8969 | 25.4983 | 90 | FALSE | 90 | 32.2222 | 100 | 57.1898 | 45 | 45 | 0.027106 | 28.4744 | 0.047397 | 48.0132
[8 empty] | 7 | 31 | 18 | 31.1111 | 1997-07-31 17:00 | 88 | 31.1111 | 47 | 72.8634 | 22.7019 | 76.6475 | 24.8042 | 88 | FALSE | 88 | 31.1111 | 100 | 58.9642 | 47 | 47 | 0.026245 | 27.5355 | 0.044509 | 45.088
[8 empty] | 7 | 31 | 19 | 30 | 1997-07-31 18:00 | 86 | 30 | 51 | 72.4503 | 22.4724 | 75.8377 | 24.3543 | 86 | FALSE | 86 | 30 | 100 | 62.1613 | 51 | 51 | 0.025968 | 27.1552 | 0.041776 | 42.3189
[8 empty] | 7 | 31 | 20 | 28.3333 | 1997-07-31 19:00 | 83 | 28.3333 | 59 | 72.2104 | 22.3391 | 74.9078 | 23.8377 | 83 | FALSE | 83 | 28.3333 | 100 | 68.3106 | 59 | 59 | 0.025923 | 26.9366 | 0.037949 | 38.4426
[8 empty] | 7 | 31 | 21 | 27.7778 | 1997-07-31 20:00 | 82 | 27.7778 | 61 | 71.8784 | 22.1547 | 74.4088 | 23.5604 | 82 | FALSE | 82 | 27.7778 | 100 | 69.86 | 61 | 61 | 0.025669 | 26.6364 | 0.036743 | 37.2212
[8 empty] | 7 | 31 | 22 | 26.6667 | 1997-07-31 21:00 | 80 | 26.6667 | 65 | 71.1559 | 21.7533 | 73.3669 | 22.9816 | 80 | FALSE | 80 | 26.6667 | 100 | 72.9397 | 65 | 65 | 0.025114 | 25.9933 | 0.034432 | 34.8792
[8 empty] | 7 | 31 | 23 | 25.5556 | 1997-07-31 22:00 | 78 | 25.5556 | 71 | 70.8763 | 21.5979 | 72.6572 | 22.5873 | 78 | FALSE | 78 | 25.5556 | 100 | 77.459 | 71 | 71 | 0.024979 | 25.7481 | 0.032247 | 32.6666
[8 empty] | 7 | 31 | 24 | 24.4444 | 1997-07-31 23:00 | 76 | 24.4444 | 79 | 70.9878 | 21.6599 | 72.2409 | 22.356 | 76 | FALSE | 76 | 24.4444 | 100 | 83.5009 | 79 | 79 | 0.025205 | 25.8457 | 0.030185 | 30.5774
[22 empty] | 84.8213 | 29.3452 | 100 |  |  | 71.8707
Formulas:
TIME = +[TIME, row above]+1/24

## conversions (hidden)
Temperature |  |  | Length |  |  | Bird Density |  |  | Flow |  |  | Velocity
English | Metric |  | English | Metric |  | English | Metric |  | English | Metric | Metric | English | Metric
C=(F-32)*.56 |  |  | 1 foot = .302 meters |  |  | (ft2/bird) | (birds/m2) |  | 1 | 1.7024 | 0.00047288 | 1 | 0.00508 | 0.018288
32 | 0 |  | 1 | 2.5417 |  | 0.4 | 26.8745 |  | 600 | 1021.4145 | 0.28373 | 100 | 0.508 | 1.8288
34 | 1.1111 |  | 2 | 5.0833 |  | 0.45 | 23.8884 |  | 50 | 85.1179 | 0.023644 | 150 | 0.762 | 2.7432
36 | 2.2222 |  | 3 | 7.625 |  | 0.5 | 21.4996 |  | 1200 | 2042.829 | 0.56745 | 200 | 1.016 | 3.6576
38 | 3.3333 |  | 4 | 10.1667 |  | 0.55 | 19.5451 |  | 2200 | 3745.1865 | 1.0403 | 250 | 1.27 | 4.572
40 | 4.4444 |  | 5 | 12.7083 |  | 0.6 | 17.9163 |  | 3200 | 5447.544 | 1.5132 | 300 | 1.524 | 5.4864
42 | 5.5556 |  | 6 | 15.25 |  | 0.65 | 16.5382 |  | 4200 | 7149.9015 | 1.9861 | 350 | 1.778 | 6.4008
44 | 6.6667 |  | 8 | 20.3333 |  | 0.7 | 15.3569 |  | 5200 | 8852.259 | 2.459 | 400 | 2.032 | 7.3152
46 | 7.7778 |  | 10 | 25.4167 |  | 0.75 | 14.3331 |  | 6200 | 10554.6165 | 2.9318 | 450 | 2.286 | 8.2296
48 | 8.8889 |  | 1 | 0.305 |  | 0.8 | 13.4372 |  | 7200 | 12256.974 | 3.4047 | 500 | 2.54 | 9.144
50 | 10 |  | 2 | 0.61 |  | 0.85 | 12.6468 |  | 8200 | 13959.3315 | 3.8776 | 550 | 2.794 | 10.0584
52 | 11.1111 |  | 3 | 0.915 |  | 0.9 | 11.9442 |  | 9200 | 15661.689 | 4.3505 | 600 | 3.048 | 10.9728
54 | 12.2222 |  | 4 | 1.22 |  | 0.95 | 11.3156 |  | 14200 | 24173.4765 | 6.7149 | 650 | 3.302 | 11.8872
56 | 13.3333 |  | 5 | 1.525 |  | 1 | 10.7498 |  | 19200 | 32685.264 | 9.0792 | 700 | 3.556 | 12.8016
58 | 14.4444 |  | 6 | 1.83 |  |  |  |  | 24200 | 41197.0515 | 11.4436 | 750 | 3.81 | 13.716
60 | 15.5556 |  | 7 | 2.135 |  | Insulation Values |  |  | 29200 | 49708.839 | 13.808 | 800 | 4.064 | 14.6304
62 | 16.6667 |  | 8 | 2.44 |  | English | Metric |  | 34200 | 58220.6265 | 16.1724 | 850 | 4.318 | 15.5448
64 | 17.7778 |  | 9 | 2.745 |  | 1 | 0.176 |  | 39200 | 66732.414 | 18.5368 | 900 | 4.572 | 16.4592
66 | 18.8889 |  | 10 | 3.05 |  | 2 | 0.352 |  | 49200 | 83755.989 | 23.2656 | 950 | 4.826 | 17.3736
68 | 20 |  | 15 | 4.575 |  | 3 | 0.528 |  | 59200 | 100779.564 | 27.9943 | 1000 | 5.08 | 18.288
70 | 21.1111 |  | 20 | 6.1 |  | 4 | 0.704 |  | 69200 | 117803.139 | 32.7231
72 | 22.2222 |  | 25 | 7.625 |  | 5 | 0.88 |  | 79200 | 134826.714 | 37.4519 | Flow
74 | 23.3333 |  | 30 | 9.15 |  | 6 | 1.056 |  | 89200 | 151850.289 | 42.1806 | English | Metric
76 | 24.4444 |  | 35 | 10.675 |  | 7 | 1.232 |  | 99200 | 168873.864 | 46.9094 | 1 | 3.79
78 | 25.5556 |  | 40 | 12.2 |  | 8 | 1.408 |  | 109200 | 185897.439 | 51.6382 | 2 | 7.58
80 | 26.6667 |  | 45 | 13.725 |  | 9 | 1.584 |  | 119200 | 202921.014 | 56.3669 | 3 | 11.37
82 | 27.7778 |  | 50 | 15.25 |  | 10 | 1.76 |  | 129200 | 219944.589 | 61.0957 | 4 | 15.16
84 | 28.8889 |  | 50 | 15.25 |  | 11 | 1.936 |  | 139200 | 236968.164 | 65.8245 | 5 | 18.95
86 | 30 |  | 100 | 30.5 |  | 12 | 2.112 |  | 149200 | 253991.739 | 70.5533 | 6 | 22.74
88 | 31.1111 |  | 150 | 45.75 |  | 13 | 2.288 |  | 159200 | 271015.314 | 75.282 | 7 | 26.53
90 | 32.2222 |  | 200 | 61 |  | 14 | 2.464 |  | 169200 | 288038.889 | 80.0108 | 8 | 30.32
92 | 33.3333 |  | 250 | 76.25 |  | 15 | 2.64 |  | 179200 | 305062.464 | 84.7396 | 9 | 34.11
94 | 34.4444 |  | 300 | 91.5 |  | 16 | 2.816 |  | 189200 | 322086.039 | 89.4683 | 10 | 37.9
96 | 35.5556 |  | 350 | 106.75 |  | 17 | 2.992 |  | 199200 | 339109.614 | 94.1971
98 | 36.6667 |  | 400 | 122 |  | 18 | 3.168 |  | 209200 | 356133.189 | 98.9259
100 | 37.7778 |  | 450 | 137.25 |  | 19 | 3.344 |  | 219200 | 373156.764 | 103.6547
102 | 38.8889 |  | 500 | 152.5 |  | 20 | 3.52 |  | 229200 | 390180.339 | 108.3834
Weight |  |  |  |  | Energy |  |  | Pressure
English | Metric | English | Metric |  | English | Metric |  | English | Metric | English | Metric
0.25 | 0.11364 | 3 | 1.3636 |  | 1 | 0.293 |  | 0.01 | 2.49 | 0.12 | 29.88
0.5 | 0.22727 | 3.25 | 1.4773 |  | 5 | 1.465 |  | 0.02 | 4.98 | 0.13 | 32.37
0.75 | 0.34091 | 3.5 | 1.5909 |  | 10 | 2.93 |  | 0.03 | 7.47 | 0.14 | 34.86
1 | 0.45455 | 3.75 | 1.7045 |  | 100 | 29.3 |  | 0.04 | 9.96 | 0.15 | 37.35
1.25 | 0.56818 | 4 | 1.8182 |  | 1000 | 293 |  | 0.05 | 12.45 | 0.16 | 39.84
1.5 | 0.68182 | 4.25 | 1.9318 |  | 10000 | 2930 |  | 0.06 | 14.94 | 0.17 | 42.33
1.75 | 0.79545 | 4.5 | 2.0455 |  | 100000 | 29300 |  | 0.07 | 17.43 | 0.18 | 44.82
2 | 0.90909 | 4.75 | 2.1591 |  |  |  |  | 0.08 | 19.92 | 0.19 | 47.31
2.25 | 1.0227 | 5 | 2.2727 |  |  |  |  | 0.09 | 22.41 | 0.2 | 49.8
2.5 | 1.1364 | 5.25 | 2.3864 |  |  |  |  | 0.1 | 24.9 | 0.21 | 52.29
2.75 | 1.25 | 5.5 | 2.5 |  |  |  |  | 0.11 | 27.39 | 0.22 | 54.78
[8 empty] | 0.12 | 29.88 | 0.23 | 57.27
[8 empty] | 0.13 | 32.37 | 0.24 | 59.76
[8 empty] | 0.14 | 34.86 | 0.25 | 62.25
[8 empty] | 0.15 | 37.35 | 0.26 | 64.74
[8 empty] | 0.16 | 39.84 | 0.27 | 67.23
[8 empty] | 0.17 | 42.33 | 0.28 | 69.72

## Sheet2 (hidden)
1000 | 20652
1000 | 20576
1200 | 21152
1500 | 22030
1905 | 22325
2521 | 23014