## Evap cooling system design
Evaportive Cooling Pad System Design 2014 - metric
The University of Georgia - Department of Poultry Science - Michael Czarick (mczarick@uga.edu)
Enter green values in all sections
Design Conditions:
Tunnel fan capacity (cmh) | 306000 |  | 180000
Outside temperature (C) | 40 |  | 104
Outside relative humidity (%) | 30
Pad height (m) | 1.53 |  | 5.0164
System Performance:
| 10 cm Pad | 15 cm Pad | 4" Pad | 6" Pad
Design pad velocity (ft/min) | 1.125 | 1.75 | 225 | 350
Minimimum recommended pad area (m2) | 74.42 | 47.8414 | 800 | 514.2857
Total pad length (m) | 48.6405 | 31.2689 | 159.4771 | 102.521
Pad static pressure (Pa) | 11.8586 | 13.3223 | 0.046687 | 0.05245
Evaporative cooling efficiency | 72.9% | 74.45%
Wet bulb / pad temperature ( C) | 25.6818 | 25.6818 | 78.2272 | 78.2272
Incoming air temperature ( C) | 29.5617 | 29.3394 | 85.2111 | 84.8109
Incoming Rh | 75.4324 | 76.6524
Pad water usage (L/min) | 33.1837 | 33.6031 | 8.7326 | 8.8429
Modify Pad Area?
| 10 cm Pad | 15 cm Pad | 4" Pad | 6" Pad
Desired total pad length (m) | 48.8 | 31.4 | 160 | 102.9508
Desired pad height (m) | 1.53 | 1.53 | 5.0164 | 5.0164
Total pad area (m2) | 74.664 | 48.042 | 802.623 | 516.4418
Pad velocity (m/sec) | 1.1213 | 1.7427 | 224.2647 | 348.5388
Pad static pressure (Pa) | 11.7906 | 13.2223 | 0.046419 | 0.052056 | 100%
Evaporative cooling efficiency | 72.95% | 74.5% | 72.95% | 74.5%
Wet bulb / pad temperature ( C) | 25.6818 | 25.6818 | 78.2272 | 78.2272
Incoming air temperature ( C) | 29.5556 | 29.3329 | 85.2 | 84.7992
Incoming Rh | 75.4659 | 76.6882
Pad water usage (l/min) | 33.1953 | 33.6153 | 8.7356 | 8.8461
Cooling efficiency |  |  | 72.95% | 74.5%
Pad velocity | 225 | 350 | 224.2647 | 348.5388
Inside temp | 85.2111 | 84.8109 | 85.2 | 84.7992
inside temp c | 29.5617 | 29.3394 | 29.5556 | 29.3329
Outside temperature | 104 | 104 | 104 | 104
Outside relative humidity | 30 | 30 | 30 | 30
Outside C | 40 | 40 | 40 | 40
Outside Rh | 30 | 30 | 30 | 30
Wet bulb (F) | 78.2272 | 78.2272 | 78.2272 | 78.2272
wet bulb C | 25.6818 | 25.6818 | 25.6818 | 25.6818
ESWB | 32.9117 | 32.9117 | 32.9117 | 32.9117
ES (inside) | 41.268 | 40.7436 | 41.2534 | 40.7284
W | 0.03073 | 0.03083 | 0.030733 | 0.030833
Ws | 0.040738 | 0.040221 | 0.040724 | 0.040206
RH (inside) | 75.4324 | 76.6524 | 75.4659 | 76.6882
pws outside | 73.8205 | 73.8205 | 73.8205 | 73.8205
pws inside | 41.3788 | 40.8518 | 41.3641 | 40.8366
pw outside | 22.1461 | 22.1461 | 22.1461 | 22.1461
pw inside | 31.213 | 31.3139 | 31.2158 | 31.3168
A outside | 0.15331 | 0.15331 | 0.15331 | 0.15331
A inside | 0.22353 | 0.22442 | 0.22356 | 0.22444
A outside english | 0.011925 | 0.011925 | 0.011925 | 0.011925
A inside english | 0.017388 | 0.017457 | 0.017389 | 0.017459
Difference | 0.0054622 | 0.0055312 | 0.0054641 | 0.0055333
gallons per minute | 8.7326 | 8.8429 | 8.7356 | 8.8461