## Evap cooling system design
Evaportive Cooling Pad System Design 2014
The University of Georgia Department of Poultry Science - Michael Czarick (mczarick@uga.edu)
Enter green values in all sections
Design Conditions:
Tunnel fan capacity (cfm) | 180000
Outside temperature (F) | 100
Outside relative humidity (%) | 20
Pad height (ft) | 5
System Performance:
| 4" Pad | 6" Pad
Design pad velocity (ft/min) | 225 | 350
Minimimum recommended pad area | 800 | 514.2857
Minimum recommended pad length | 160 | 102.8571
Pad static pressure | 0.046687 | 0.05245
Evaporative cooling efficiency | 72.9% | 74.45%
Wet bulb / pad temperature | 70.923 | 70.923
Incoming air temperature | 78.8023 | 78.3507
Incoming Rh | 71.0567 | 72.4549
Pad water usage | 10.1671 | 10.2853
Modify Pad Area?
| 4" Pad | 6" Pad
Desired total pad length (ft) | 160 | 103
Desired pad height (ft) | 5 | 5
Total pad area | 800 | 515
Pad velocity | 225 | 349.5146
Pad static pressure | 0.046687 | 0.052319
Evaporative cooling efficiency | 72.9% | 74.47%
Wet bulb / pad temperature | 70.923 | 70.923
Incoming air temperature | 78.8023 | 78.3464
Incoming Rh | 71.0567 | 72.4685
Pad water usage | 10.1671 | 10.2864
Cooling efficiency |  |  | 72.9% | 74.47%
Pad velocity | 225 | 350 | 225 | 349.5146
Inside temp | 78.8023 | 78.3507 | 78.8023 | 78.3464
inside temp c | 26.0013 | 25.7504 | 26.0013 | 25.748
Outside temperature | 100 | 100 | 100 | 100
Outside relative humidity | 20 | 20 | 20 | 20
Outside C | 37.7778 | 37.7778 | 37.7778 | 37.7778
Outside Rh | 20 | 20 | 20 | 20
Wet bulb (F) | 70.923 | 70.923 | 70.923 | 70.923
wet bulb C | 21.6239 | 21.6239 | 21.6239 | 21.6239
ESWB | 25.789 | 25.789 | 25.789 | 25.789
ES (inside) | 33.539 | 33.0456 | 33.539 | 33.0408
W | 0.023526 | 0.023636 | 0.023526 | 0.023637
Ws | 0.033109 | 0.032621 | 0.033109 | 0.032617
RH (inside) | 71.0567 | 72.4549 | 71.0567 | 72.4685
pws outside | 65.499 | 65.499 | 65.499 | 65.499
pws inside | 33.6144 | 33.1189 | 33.6144 | 33.1142
pw outside | 13.0998 | 13.0998 | 13.0998 | 13.0998
pw inside | 23.8853 | 23.9963 | 23.8853 | 23.9973
A outside | 0.091334 | 0.091334 | 0.091334 | 0.091334
A inside | 0.17309 | 0.17404 | 0.17309 | 0.17405
A outside english | 0.0071045 | 0.0071045 | 0.0071045 | 0.0071045
A inside english | 0.013464 | 0.013538 | 0.013464 | 0.013539
Difference | 0.0063595 | 0.0064334 | 0.0063595 | 0.0064342
gallons per minute | 10.1671 | 10.2853 | 10.1671 | 10.2864